## LineData
FROM | TO | D | TYPE | FIELD
8284 | 8287 | 0.02449 | 1 | 101
8287 | 8286 | 0.3172 | 1
8286 | 8285 | 0.213 | 1
8285 | 3740 | 0.50174 | 1
3740 | 2064 | 0.4403 | 1
4414 | 2036 | 0.2514 | 1
2036 | 2040 | 0.1534 | 1
2040 | 4446 | 0.43205 | 1
4446 | 3704 | 0.05211 | 1
3704 | 2035 | 0.383 | 1
2035 | 2661 | 0.44871 | 1
2661 | 3917 | 0.36501 | 1
3917 | 4494 | 0.07745 | 1
4494 | 4402 | 0.25081 | 1
4402 | 8284 | 0.01048 | 1 | 211
8284 | 3703 | 1.2473 | 1 | 103
3703 | 8561 | 0.2438 | 1
8561 | 3784 | 0.3846 | 1
3915 | 4980 | 0.22 | 1
4980 | 3912 | 0.1166 | 1
3912 | 4452 | 0.2633 | 1
4452 | 8284 | 0.6197 | 1 | 214
8284 | 6990 | 2.3973 | 2 | 210
6990 | 7710 | 0.2027 | 3 | 302
7710 | 7433 | 3.5589 | 2 | 301
7433 | 7490 | 0.1672 | 2
7490 | 3181 | 0.01547 | 4
7710 | 4427 | 0.71437 | 5 | 101
4427 | 3547 | 0.32383 | 5
3547 | 3939 | 1.0754 | 5
8284 | 7076 | 0.5858 | 6 | 104
8284 | 3073 | 0.3539 | 1 | 102
3073 | 3980 | 0.54522 | 1
3980 | 4081 | 0.1163 | 1
8419 | 4550 | 0.1817 | 1
4550 | 4281 | 0.05268 | 1
4281 | 3982 | 0.007793 | 1
3982 | 8284 | 0.47657 | 1 | 212
8284 | 8288 | 0.2795 | 1 | 213
8288 | 8289 | 0.2835 | 1
8289 | 4557 | 0.1719 | 1
4557 | 8290 | 0.245 | 1
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: km

## CableTypes
TYPE | R | X | B | INFO | IRATED | VRATED
1 | 0.126 | 0.116 | 91.1062 | 240 AL XLPE 12/20 trefoil | 0.375 | 20
2 | 0.387 | 0.088 | 87.9646 | 50 CU GPLK 8/10 | 0.16 | 10
3 | 0.322 | 0.102 | 100.531 | 95 AL Kudi 6/10 | 0.215 | 10
4 | 0.126 | 0.123 | 69.115 | 240 AL XLPE 18/30 trefoil | 0.38 | 30
5 | 1.2 | 0.099 | 69.115 | 25 CU GPLK 10/10 | 0.082 | 10
6 | 0.049 | 0.106 | 201.0619 | 630 AL XLPE 18/30 trefoil | 0.6 | 30
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ohm/km - ohm/km - uS/km
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kA
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kV

## NodeData
NODES | Tb | Smax
8284 | 1 | 20784.6097
8287 | 0 | 400
8286 | 0 | 400
8285 | 0 | 400
3740 | 0 | 1000
2064 | 0 | 400
4414 | 0 | 2000
2036 | 0 | 400
2040 | 0 | 630
4446 | 0 | 1750
3704 | 0 | 630
2035 | 0 | 400
2661 | 0 | 630
3917 | 0 | 1600
4494 | 0 | 1000
4402 | 0 | 1600
3703 | 0 | 1600
8561 | 0 | 250
3784 | 0 | 1000
3915 | 0 | 1600
4980 | 0 | 400
3912 | 0 | 1600
4452 | 0 | 1600
6990 | 0 | 100
7710 | 0 | 1600
7433 | 0 | 100
7490 | 0 | 100
3181 | 0 | 400
4427 | 0 | 400
3547 | 0 | 250
3939 | 0 | 100
3073 | 0 | 400
3980 | 0 | 1000
4081 | 0 | 630
8419 | 0 | 2000
4550 | 0 | 1600
4281 | 0 | 2000
3982 | 0 | 2000
8288 | 0 | 400
8289 | 0 | 400
4557 | 0 | 400
8290 | 0 | 400
7076 | 0 | 10392.3048
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kVA
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: sqrt(3)*Inom*Vnom*2 (2 cables)

## PVData
NODES | PPV | QPV | S | pf
3917 | 1440 | 0 | 1440 | 1
7710 | 250 | 0 | 250 | 1
3073 | 350 | 0 | 350 | 1
8419 | 1000 | 0 | 1000 | 1
8288 | 40 | 0 | 40 | 1
8561 | 100 | 0 | 100 | 1
2035 | 80 | 0 | 80 | 1
8289 | 110 | 0 | 110 | 1
3704 | 600 | 0 | 600 | 1
4081 | 688 | 0 | 688 | 1
4281 | 1479 | 0 | 1479 | 1
3982 | 1450 | 0 | 1450 | 1

## PVGeneration
TIME | QPV | mean | variance
1 | 0 | 0 | 0
2 | 0 | 0 | 0
3 | 0 | 0 | 0
4 | 0 | 0 | 0
5 | 0 | 0.0515 | 0.0138
6 | 0 | 0.1278 | 0.0406
7 | 0 | 0.2538 | 0.0714
8 | 0 | 0.3824 | 0.1189
9 | 0 | 0.4908 | 0.1388
10 | 0 | 0.568 | 0.1659
11 | 0 | 0.6164 | 0.1445
12 | 0 | 0.599 | 0.1175
13 | 0 | 0.5614 | 0.0995
14 | 0 | 0.4672 | 0.0788
15 | 0 | 0.3548 | 0.055
16 | 0 | 0.2228 | 0.041
17 | 0 | 0.103 | 0.0276
18 | 0 | 0 | 0
19 | 0 | 0 | 0
20 | 0 | 0 | 0
21 | 0 | 0 | 0
22 | 0 | 0 | 0
23 | 0 | 0 | 0
24 | 0 | 0 | 0
25 | 0 | 0 | 0
26 | 0 | 0 | 0
27 | 0 | 0 | 0
28 | 0 | 0 | 0
29 | 0 | 0.0515 | 0.0138
30 | 0 | 0.1278 | 0.0406
31 | 0 | 0.2538 | 0.0714
32 | 0 | 0.3824 | 0.1189
33 | 0 | 0.4908 | 0.1388
34 | 0 | 0.568 | 0.1659
35 | 0 | 0.6164 | 0.1445
36 | 0 | 0.599 | 0.1175
37 | 0 | 0.5614 | 0.0995
38 | 0 | 0.4672 | 0.0788
39 | 0 | 0.3548 | 0.055
40 | 0 | 0.2228 | 0.041
41 | 0 | 0.103 | 0.0276
42 | 0 | 0 | 0
43 | 0 | 0 | 0
44 | 0 | 0 | 0
45 | 0 | 0 | 0
46 | 0 | 0 | 0
47 | 0 | 0 | 0
48 | 0 | 0 | 0
49 | 0 | 0 | 0
50 | 0 | 0 | 0
51 | 0 | 0 | 0
52 | 0 | 0 | 0
53 | 0 | 0.0515 | 0.0138
54 | 0 | 0.1278 | 0.0406
55 | 0 | 0.2538 | 0.0714
56 | 0 | 0.3824 | 0.1189
57 | 0 | 0.4908 | 0.1388
58 | 0 | 0.568 | 0.1659
59 | 0 | 0.6164 | 0.1445
60 | 0 | 0.599 | 0.1175
61 | 0 | 0.5614 | 0.0995
62 | 0 | 0.4672 | 0.0788
63 | 0 | 0.3548 | 0.055
64 | 0 | 0.2228 | 0.041
65 | 0 | 0.103 | 0.0276
66 | 0 | 0 | 0
67 | 0 | 0 | 0
68 | 0 | 0 | 0
69 | 0 | 0 | 0
70 | 0 | 0 | 0
71 | 0 | 0 | 0
72 | 0 | 0 | 0
73 | 0 | 0 | 0
74 | 0 | 0 | 0
75 | 0 | 0 | 0
76 | 0 | 0 | 0
77 | 0 | 0.0515 | 0.0138
78 | 0 | 0.1278 | 0.0406
79 | 0 | 0.2538 | 0.0714
80 | 0 | 0.3824 | 0.1189
81 | 0 | 0.4908 | 0.1388
82 | 0 | 0.568 | 0.1659
83 | 0 | 0.6164 | 0.1445
84 | 0 | 0.599 | 0.1175
85 | 0 | 0.5614 | 0.0995
86 | 0 | 0.4672 | 0.0788
87 | 0 | 0.3548 | 0.055
88 | 0 | 0.2228 | 0.041
89 | 0 | 0.103 | 0.0276
90 | 0 | 0 | 0
91 | 0 | 0 | 0
92 | 0 | 0 | 0
93 | 0 | 0 | 0
94 | 0 | 0 | 0
95 | 0 | 0 | 0
96 | 0 | 0 | 0
97 | 0 | 0 | 0
98 | 0 | 0 | 0
99 | 0 | 0 | 0
100 | 0 | 0 | 0
101 | 0 | 0.0515 | 0.0138
102 | 0 | 0.1278 | 0.0406
103 | 0 | 0.2538 | 0.0714
104 | 0 | 0.3824 | 0.1189
105 | 0 | 0.4908 | 0.1388
106 | 0 | 0.568 | 0.1659
107 | 0 | 0.6164 | 0.1445
108 | 0 | 0.599 | 0.1175
109 | 0 | 0.5614 | 0.0995
110 | 0 | 0.4672 | 0.0788
111 | 0 | 0.3548 | 0.055
112 | 0 | 0.2228 | 0.041
113 | 0 | 0.103 | 0.0276
114 | 0 | 0 | 0
115 | 0 | 0 | 0
116 | 0 | 0 | 0
117 | 0 | 0 | 0
118 | 0 | 0 | 0
119 | 0 | 0 | 0
120 | 0 | 0 | 0
121 | 0 | 0 | 0
122 | 0 | 0 | 0
123 | 0 | 0 | 0
124 | 0 | 0 | 0
125 | 0 | 0.0515 | 0.0138
126 | 0 | 0.1278 | 0.0406
127 | 0 | 0.2538 | 0.0714
128 | 0 | 0.3824 | 0.1189
129 | 0 | 0.4908 | 0.1388
130 | 0 | 0.568 | 0.1659
131 | 0 | 0.6164 | 0.1445
132 | 0 | 0.599 | 0.1175
133 | 0 | 0.5614 | 0.0995
134 | 0 | 0.4672 | 0.0788
135 | 0 | 0.3548 | 0.055
136 | 0 | 0.2228 | 0.041
137 | 0 | 0.103 | 0.0276
138 | 0 | 0 | 0
139 | 0 | 0 | 0
140 | 0 | 0 | 0
141 | 0 | 0 | 0
142 | 0 | 0 | 0
143 | 0 | 0 | 0
144 | 0 | 0 | 0
145 | 0 | 0 | 0
146 | 0 | 0 | 0
147 | 0 | 0 | 0
148 | 0 | 0 | 0
149 | 0 | 0.0515 | 0.0138
150 | 0 | 0.1278 | 0.0406
151 | 0 | 0.2538 | 0.0714
152 | 0 | 0.3824 | 0.1189
153 | 0 | 0.4908 | 0.1388
154 | 0 | 0.568 | 0.1659
155 | 0 | 0.6164 | 0.1445
156 | 0 | 0.599 | 0.1175
157 | 0 | 0.5614 | 0.0995
158 | 0 | 0.4672 | 0.0788
159 | 0 | 0.3548 | 0.055
160 | 0 | 0.2228 | 0.041
161 | 0 | 0.103 | 0.0276
162 | 0 | 0 | 0
163 | 0 | 0 | 0
164 | 0 | 0 | 0
165 | 0 | 0 | 0
166 | 0 | 0 | 0
167 | 0 | 0 | 0
168 | 0 | 0 | 0
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: summer Reply: kW/m^2

## WindData
NODES | PWT | QWT
7076 | 9843 | 0

## WindGeneration
TIME | QWT | mean | variance
1 | 0 | 9.9 | 0.7937
2 | 0 | 9.3667 | 0.8021
3 | 0 | 9.1667 | 0.8505
4 | 0 | 9 | 0.8185
5 | 0 | 8.7 | 0.755
6 | 0 | 8.6 | 1.0583
7 | 0 | 9 | 1.1533
8 | 0 | 9.0333 | 1.1504
9 | 0 | 9.3333 | 0.9504
10 | 0 | 9.6 | 1.1533
11 | 0 | 10.1333 | 1.0066
12 | 0 | 10.2667 | 0.8622
13 | 0 | 7.9667 | 0.3786
14 | 0 | 8 | 0.4583
15 | 0 | 8 | 0.5
16 | 0 | 7.7333 | 0.4509
17 | 0 | 6.9667 | 0.2309
18 | 0 | 5.9667 | 0.3786
19 | 0 | 4.8333 | 0.3215
20 | 0 | 4.4333 | 0.3215
21 | 0 | 4.3333 | 0.4163
22 | 0 | 4.1 | 0.2646
23 | 0 | 4.0667 | 0.2082
24 | 0 | 4 | 0.1732
25 | 0 | 9.9 | 0.7937
26 | 0 | 9.3667 | 0.8021
27 | 0 | 9.1667 | 0.8505
28 | 0 | 9 | 0.8185
29 | 0 | 8.7 | 0.755
30 | 0 | 8.6 | 1.0583
31 | 0 | 9 | 1.1533
32 | 0 | 9.0333 | 1.1504
33 | 0 | 9.3333 | 0.9504
34 | 0 | 9.6 | 1.1533
35 | 0 | 10.1333 | 1.0066
36 | 0 | 10.2667 | 0.8622
37 | 0 | 7.9667 | 0.3786
38 | 0 | 8 | 0.4583
39 | 0 | 8 | 0.5
40 | 0 | 7.7333 | 0.4509
41 | 0 | 6.9667 | 0.2309
42 | 0 | 5.9667 | 0.3786
43 | 0 | 4.8333 | 0.3215
44 | 0 | 4.4333 | 0.3215
45 | 0 | 4.3333 | 0.4163
46 | 0 | 4.1 | 0.2646
47 | 0 | 4.0667 | 0.2082
48 | 0 | 4 | 0.1732
49 | 0 | 9.9 | 0.7937
50 | 0 | 9.3667 | 0.8021
51 | 0 | 9.1667 | 0.8505
52 | 0 | 9 | 0.8185
53 | 0 | 8.7 | 0.755
54 | 0 | 8.6 | 1.0583
55 | 0 | 9 | 1.1533
56 | 0 | 9.0333 | 1.1504
57 | 0 | 9.3333 | 0.9504
58 | 0 | 9.6 | 1.1533
59 | 0 | 10.1333 | 1.0066
60 | 0 | 10.2667 | 0.8622
61 | 0 | 7.9667 | 0.3786
62 | 0 | 8 | 0.4583
63 | 0 | 8 | 0.5
64 | 0 | 7.7333 | 0.4509
65 | 0 | 6.9667 | 0.2309
66 | 0 | 5.9667 | 0.3786
67 | 0 | 4.8333 | 0.3215
68 | 0 | 4.4333 | 0.3215
69 | 0 | 4.3333 | 0.4163
70 | 0 | 4.1 | 0.2646
71 | 0 | 4.0667 | 0.2082
72 | 0 | 4 | 0.1732
73 | 0 | 9.9 | 0.7937
74 | 0 | 9.3667 | 0.8021
75 | 0 | 9.1667 | 0.8505
76 | 0 | 9 | 0.8185
77 | 0 | 8.7 | 0.755
78 | 0 | 8.6 | 1.0583
79 | 0 | 9 | 1.1533
80 | 0 | 9.0333 | 1.1504
81 | 0 | 9.3333 | 0.9504
82 | 0 | 9.6 | 1.1533
83 | 0 | 10.1333 | 1.0066
84 | 0 | 10.2667 | 0.8622
85 | 0 | 7.9667 | 0.3786
86 | 0 | 8 | 0.4583
87 | 0 | 8 | 0.5
88 | 0 | 7.7333 | 0.4509
89 | 0 | 6.9667 | 0.2309
90 | 0 | 5.9667 | 0.3786
91 | 0 | 4.8333 | 0.3215
92 | 0 | 4.4333 | 0.3215
93 | 0 | 4.3333 | 0.4163
94 | 0 | 4.1 | 0.2646
95 | 0 | 4.0667 | 0.2082
96 | 0 | 4 | 0.1732
97 | 0 | 9.9 | 0.7937
98 | 0 | 9.3667 | 0.8021
99 | 0 | 9.1667 | 0.8505
100 | 0 | 9 | 0.8185
101 | 0 | 8.7 | 0.755
102 | 0 | 8.6 | 1.0583
103 | 0 | 9 | 1.1533
104 | 0 | 9.0333 | 1.1504
105 | 0 | 9.3333 | 0.9504
106 | 0 | 9.6 | 1.1533
107 | 0 | 10.1333 | 1.0066
108 | 0 | 10.2667 | 0.8622
109 | 0 | 7.9667 | 0.3786
110 | 0 | 8 | 0.4583
111 | 0 | 8 | 0.5
112 | 0 | 7.7333 | 0.4509
113 | 0 | 6.9667 | 0.2309
114 | 0 | 5.9667 | 0.3786
115 | 0 | 4.8333 | 0.3215
116 | 0 | 4.4333 | 0.3215
117 | 0 | 4.3333 | 0.4163
118 | 0 | 4.1 | 0.2646
119 | 0 | 4.0667 | 0.2082
120 | 0 | 4 | 0.1732
121 | 0 | 9.9 | 0.7937
122 | 0 | 9.3667 | 0.8021
123 | 0 | 9.1667 | 0.8505
124 | 0 | 9 | 0.8185
125 | 0 | 8.7 | 0.755
126 | 0 | 8.6 | 1.0583
127 | 0 | 9 | 1.1533
128 | 0 | 9.0333 | 1.1504
129 | 0 | 9.3333 | 0.9504
130 | 0 | 9.6 | 1.1533
131 | 0 | 10.1333 | 1.0066
132 | 0 | 10.2667 | 0.8622
133 | 0 | 7.9667 | 0.3786
134 | 0 | 8 | 0.4583
135 | 0 | 8 | 0.5
136 | 0 | 7.7333 | 0.4509
137 | 0 | 6.9667 | 0.2309
138 | 0 | 5.9667 | 0.3786
139 | 0 | 4.8333 | 0.3215
140 | 0 | 4.4333 | 0.3215
141 | 0 | 4.3333 | 0.4163
142 | 0 | 4.1 | 0.2646
143 | 0 | 4.0667 | 0.2082
144 | 0 | 4 | 0.1732
145 | 0 | 9.9 | 0.7937
146 | 0 | 9.3667 | 0.8021
147 | 0 | 9.1667 | 0.8505
148 | 0 | 9 | 0.8185
149 | 0 | 8.7 | 0.755
150 | 0 | 8.6 | 1.0583
151 | 0 | 9 | 1.1533
152 | 0 | 9.0333 | 1.1504
153 | 0 | 9.3333 | 0.9504
154 | 0 | 9.6 | 1.1533
155 | 0 | 10.1333 | 1.0066
156 | 0 | 10.2667 | 0.8622
157 | 0 | 7.9667 | 0.3786
158 | 0 | 8 | 0.4583
159 | 0 | 8 | 0.5
160 | 0 | 7.7333 | 0.4509
161 | 0 | 6.9667 | 0.2309
162 | 0 | 5.9667 | 0.3786
163 | 0 | 4.8333 | 0.3215
164 | 0 | 4.4333 | 0.3215
165 | 0 | 4.3333 | 0.4163
166 | 0 | 4.1 | 0.2646
167 | 0 | 4.0667 | 0.2082
168 | 0 | 4 | 0.1732
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: summer Reply: m/s

## Storages
NODES | Power | Energy | SOEini | Eff

## DGs
NODES | FC | H | eff | pf | Rup | Rdw | Smax

## AggData
AGG | PD | pf | RU | RD | PDini | E Summer | PDmin | NOTE | In report | Name | Type | Status | Load profile | Connections | Comment
2035 | 0.033 | 0.98 | 1000 | -1000 | 0.01056 | 0.167 | 0.001 |  | yes |  | Distribution station | In use | Measurement | 1 | Client: Van Den Heuvel.
2036 | 0.0353 | 0.98 | 1000 | -1000 | 0.011296 | 0.3257 | 0.0084 |  | yes |  | Distribution station | In use | NEDU | 7 | Households.
2040 | 0.0049 | 0.98 | 1000 | -1000 | 0.001568 | 0.0636 | 0.0016 |  | yes |  | Distribution station | In use | None | 0 | No connections yet.
2064 | 0 | 0.98 | 1000 | -1000 | 0 | 0 | 0 | NO LOAD | yes |  | Distribution station | In use | None | 1 | Temporary connection.
2661 | 0.162 | 0.98 | 1000 | -1000 | 0.05184 | 2.547 | 0.023 | G - 1216 kW | yes |  | Client station | In use | Measurement | 1 | Client: DHL Distribution centre.
3073 | 0.191 | 0.98 | 1000 | -1000 | 0.06112 | 1.419 | 0 | PV + DEM | yes |  | Client station | In use | Measurement | 1 | Client: PostNL Distribution centre.
3181 | 0.076 | 0.98 | 1000 | -1000 | 0.02432 | 0.713 | 0.014 |  | yes |  | Client station | In use | None | 1 | Temporary connection.
3547 | 0.1686 | 0.98 | 1000 | -1000 | 0.053952 | 1.6634 | 0.04 |  | yes |  | Distribution station | In use | NEDU | 158 | 158 households in Tull en het Waal, some with PV.
3703 | 0.08 | 0.98 | 1000 | -1000 | 0.0256 | 0.105 | 0.004 |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
3704 | 0.073 | 0.98 | 1000 | -1000 | 0.02336 | 1.087 | 0.002 |  | yes |  | Client station | In use | Constructed | 0 | New EPG Distribution centre at Peletonsdok 1. Nog measurements yet. Profile constructed based on DHL measurement data.
3740 | 0.09 | 0.98 | 1000 | -1000 | 0.0288 | 1.361 | 0.038 |  | yes |  | Client station | Planned | Constructed | 0 | Planned client station Sluispad. Likely for the new lock system (Prinses Beatrixsluizen)
3784 | 0.11 | 0.98 | 1000 | -1000 | 0.0352 | 0.142 | 0.001 |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
3912 | 0.09 | 0.98 | 1000 | -1000 | 0.0288 | 0.081 | 0 |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
3915 | 0.031 | 0.98 | 1000 | -1000 | 0.00992 | 0.026 | 0 |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
3917 | 0 | 0.98 | 1000 | -1000 | 0 | 0 | 0 | PV | yes |  | Client station | Planned | None | 0 | Likely second connection at DHL Distribution centre for rooftop PV system. (1.44 MWp planned.)
3939 | 0.005 | 0.98 | 1000 | -1000 | 0.0016 | 0.5581 | 0.15 |  | yes |  | Distribution station | In use | NEDU | 38 | 38 households in Tull en het Waal, some with PV.
3980 | 0.163 | 0.98 | 1000 | -1000 | 0.05216 | 1.283 | 0.007 |  | yes |  | Client station | Planned | None | 0 | Planned station Ravelijndok. Likely to connect building Ravelijndok 1 BAG 0356100000125368.
3982 | 0 | 0.98 | 1000 | -1000 | 0 | ? | ? | G - 1450 kW | yes |  | Client station | Planned | None | 0 | Likely second connection at PEC Distribution centre for rooftop PV system. (3.8 MWp planned.)
4081 | 0 | 0.98 | 1000 | -1000 | 0 | ? | ? | G - 688 kW | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4281 | 0 | 0.98 | 1000 | -1000 | 0 | ? | ? | G - 1479 kW | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4402 | 0.593 | 0.98 | 1000 | -1000 | 0.18976 | ? | ? |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4414 | 0.629 | 0.98 | 1000 | -1000 | 0.20128 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4427 | 0 | 0.98 | 1000 | -1000 | 0 | 0 | 0 | NO LOAD | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4446 | 0.23 | 0.98 | 1000 | -1000 | 0.0736 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4452 | 0.278 | 0.98 | 1000 | -1000 | 0.08896 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4494 | 0.001 | 0.98 | 1000 | -1000 | 0.00032 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4550 | 0.151 | 0.98 | 1000 | -1000 | 0.04832 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4557 | 0.005 | 0.98 | 1000 | -1000 | 0.0016 | ? | ? | NO PROFILE | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
4980 | 0.26 | 0.98 | 1000 | -1000 | 0.0832 | 2.7374 | 0.0334 |  | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
6990 | 0.0625 | 0.98 | 1000 | -1000 | 0.02 | 0.6766 | 0.02 |  | yes |  | Distribution station | In use | NEDU | 31 | centre for rooftop PV system. (3.8 MWp planned.) 6990 WAALSEWEG 4 Distribution station In use NEDU 31
7076 | 0.07 | 0.98 | 1000 | -1000 | 0.0224 | 0.136 | 0 | WIND + DEM | yes |  | Client station | In use | None | 1 | Client: Windmolenpark Nieuwegein. (5 wind turbines, total 10 MW.)
7433 | 0.016 | 0.98 | 1000 | -1000 | 0.00512 | 0.1508 | 0.004 |  | yes |  | Distribution station | In use | NEDU | 22 | 22 households in Ossenwaard.
7490 | 0.0003 | 0.98 | 1000 | -1000 | 9.6e-05 | 0.0025 | 0.0001 |  | yes |  | Distribution station | In use | None | 3 | 2 connections with measurement data. Measurements show no activity. 1 connection with negligible energy use.
7710 | 0.3 | 0.98 | 1000 | -1000 | 0.096 | 0.14 | 5.5 | PV + DEM | yes |  | Client station | In use | Measurement | 1 | Client: Vitens water treatment plant.
8284 | 0 | 1 | 1000 | -1000 | 0 |  | 0 | SLACK | no |  | Unknown | Unknown | Unknown | Unknown | Unknown
8285 | 0.0016 | 0.98 | 1000 | -1000 | 0.000512 | 0.013 | 0.0004 |  | yes |  | Distribution station | In use | None | 2 | 2 connections with negligible energy use.
8286 | 0.0323 | 0.98 | 1000 | -1000 | 0.010336 | 0.4215 | 0.0105 |  | yes |  | Distribution station | In use | NEDU | 3 | 2 connections NEDU, 1 temporary connection.
8287 | 0.0589 | 0.98 | 1000 | -1000 | 0.018848 | 0.977 | 0.0088 |  | yes |  | Distribution station | In use | Combined | 7 | 6 connections NEDU, 1 connection with measurements; gas station BP.
8288 | 0.0407 | 0.98 | 1000 | -1000 | 0.013024 | 0.1158 | 0 |  | yes |  | Distribution station | In use | None | 2 | Temporary connection at construction site.
8289 | 0.055 | 0.98 | 1000 | -1000 | 0.0176 | 0.507 | 0.0063 |  | yes |  | Distribution station | In use | Combined | 3 | 1 connection NEDU, 2 connections with measurements.
8290 | 0.0325 | 0.98 | 1000 | -1000 | 0.0104 | 0.4151 | 0.0104 |  | yes |  | Distribution station | In use | NEDU | 6 | 5 connections NEDU, 1 connection measured, however negligible energy used, not simulated.
8419 | 0.24 | 0.98 | 1000 | -1000 | 0.0768 | 1.768 | 0 | PV + DEM | yes |  | Client station | In use | Measurement | 1 | Client: Fiege Distribution centre.
8561 | 0.041 | 0.98 | 1000 | -1000 | 0.01312 | 0.236 | 0.001 |  | yes |  | Distribution station | In use | None | 1 | 1 connection with PV. No load information available. Load not simulated.
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kW Reply: MW
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kW Reply: MW
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MWh Reply: for single day ~ 19.7.2019

## DemandBlocks
DB | MargUtil | AGG
d1 | 56 | 8284
d2 | 52 | 8284
d3 | 51 | 8284
d4 | 46 | 8284
d5 | 61 | 8287
d6 | 56 | 8287
d7 | 52 | 8287
d8 | 46 | 8287
d9 | 59 | 8286
d10 | 56 | 8286
d11 | 52 | 8286
d12 | 47 | 8286
d13 | 56 | 8285
d14 | 52 | 8285
d15 | 51 | 8285
d16 | 46 | 8285
d17 | 61 | 3740
d18 | 56 | 3740
d19 | 52 | 3740
d20 | 46 | 3740
d21 | 59 | 2064
d22 | 56 | 2064
d23 | 52 | 2064
d24 | 47 | 2064
d25 | 56 | 4414
d26 | 52 | 4414
d27 | 51 | 4414
d28 | 46 | 4414
d29 | 61 | 2036
d30 | 56 | 2036
d31 | 52 | 2036
d32 | 46 | 2036
d33 | 59 | 2040
d34 | 56 | 2040
d35 | 52 | 2040
d36 | 47 | 2040
d37 | 56 | 4446
d38 | 52 | 4446
d39 | 51 | 4446
d40 | 46 | 4446
d41 | 61 | 3704
d42 | 56 | 3704
d43 | 52 | 3704
d44 | 46 | 3704
d45 | 59 | 2035
d46 | 56 | 2035
d47 | 52 | 2035
d48 | 47 | 2035
d49 | 56 | 2661
d50 | 52 | 2661
d51 | 51 | 2661
d52 | 46 | 2661
d53 | 61 | 3917
d54 | 56 | 3917
d55 | 52 | 3917
d56 | 46 | 3917
d57 | 59 | 4494
d58 | 56 | 4494
d59 | 52 | 4494
d60 | 47 | 4494
d61 | 56 | 4402
d62 | 52 | 4402
d63 | 51 | 4402
d64 | 46 | 4402
d65 | 61 | 3703
d66 | 56 | 3703
d67 | 52 | 3703
d68 | 46 | 3703
d69 | 59 | 8561
d70 | 56 | 8561
d71 | 52 | 8561
d72 | 47 | 8561
d73 | 56 | 3784
d74 | 52 | 3784
d75 | 51 | 3784
d76 | 46 | 3784
d77 | 61 | 3915
d78 | 56 | 3915
d79 | 52 | 3915
d80 | 46 | 3915
d81 | 59 | 4980
d82 | 56 | 4980
d83 | 52 | 4980
d84 | 47 | 4980
d85 | 56 | 3912
d86 | 52 | 3912
d87 | 51 | 3912
d88 | 46 | 3912
d89 | 61 | 4452
d90 | 56 | 4452
d91 | 52 | 4452
d92 | 46 | 4452
d93 | 59 | 6990
d94 | 56 | 6990
d95 | 52 | 6990
d96 | 47 | 6990
d97 | 56 | 7710
d98 | 52 | 7710
d99 | 51 | 7710
d100 | 46 | 7710
d101 | 61 | 7433
d102 | 56 | 7433
d103 | 52 | 7433
d104 | 46 | 7433
d105 | 59 | 7490
d106 | 56 | 7490
d107 | 52 | 7490
d108 | 47 | 7490
d109 | 56 | 3181
d110 | 52 | 3181
d111 | 51 | 3181
d112 | 46 | 3181
d113 | 61 | 4427
d114 | 56 | 4427
d115 | 52 | 4427
d116 | 46 | 4427
d117 | 59 | 3547
d118 | 56 | 3547
d119 | 52 | 3547
d120 | 47 | 3547
d121 | 56 | 3939
d122 | 52 | 3939
d123 | 51 | 3939
d124 | 46 | 3939
d125 | 61 | 3073
d126 | 56 | 3073
d127 | 52 | 3073
d128 | 46 | 3073
d129 | 59 | 3980
d130 | 56 | 3980
d131 | 52 | 3980
d132 | 47 | 3980
d133 | 56 | 4081
d134 | 52 | 4081
d135 | 51 | 4081
d136 | 46 | 4081
d137 | 56 | 8419
d138 | 52 | 8419
d139 | 51 | 8419
d140 | 46 | 8419
d141 | 56 | 4550
d142 | 52 | 4550
d143 | 51 | 4550
d144 | 46 | 4550
d145 | 59 | 4281
d146 | 56 | 4281
d147 | 52 | 4281
d148 | 47 | 4281
d149 | 59 | 3982
d150 | 56 | 3982
d151 | 52 | 3982
d152 | 47 | 3982
d153 | 61 | 8288
d154 | 56 | 8288
d155 | 52 | 8288
d156 | 46 | 8288
d157 | 61 | 8289
d158 | 56 | 8289
d159 | 52 | 8289
d160 | 46 | 8289
d161 | 56 | 4557
d162 | 52 | 4557
d163 | 51 | 4557
d164 | 46 | 4557
d165 | 56 | 8290
d166 | 52 | 8290
d167 | 51 | 8290
d168 | 46 | 8290
d169 | 59 | 7076
d170 | 56 | 7076
d171 | 52 | 7076
d172 | 47 | 7076
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: fiat/MWh

## UtilTimeMul
TIME | UtilMultiplier | Price
1 | 0.8 | 40
2 | 0.78 | 40
3 | 0.72 | 40
4 | 0.71 | 45
5 | 0.76 | 50
6 | 0.97 | 55
7 | 1.1 | 55
8 | 1.2 | 55
9 | 0.95 | 50
10 | 0.91 | 50
11 | 0.86 | 50
12 | 0.82 | 50
13 | 0.8 | 50
14 | 0.94 | 50
15 | 0.95 | 50
16 | 1.03 | 50
17 | 1.19 | 50
18 | 1.25 | 60
19 | 1.23 | 60
20 | 1.18 | 60
21 | 1.03 | 60
22 | 0.99 | 60
23 | 0.92 | 60
24 | 0.84 | 60
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: fiat/MWh

## SystemDemand
| TIME | 8284 | 8287 | 8286 | 8285 | 3740 | 2064 | 4414 | 2036 | 2040 | 4446 | 3704 | 2035 | 2661 | 3917 | 4494 | 4402 | 3703 | 8561 | 3784 | 3915 | 4980 | 3912 | 4452 | 6990 | 7710 | 7433 | 7490 | 3181 | 4427 | 3547 | 3939 | 3073 | 3980 | 4081 | 8419 | 4550 | 4281 | 3982 | 8288 | 8289 | 4557 | 8290 | 7076
2019-07-15 | 1 | 0 | 0.033 | 0.0154 | 0.0006 | 0.06 | 0 | 0.1 | 0.0137 | 0.0025 | 0.04 | 0.038 | 0.003 | 0.062 | 0 | 0.001 | 0.1 | 0 | 0.01 | 0.001 | 0 | 0.0382 | 0 | 0.04 | 0.0269 | 0.228 | 0.0063 | 0.0001 | 0.023 | 0 | 0.0681 | 0.0219 | 0.108 | 0.015 | 0 | 0.135 | 0.04 | 0 | 0 | 0.007 | 0.008 | 0.005 | 0.0151 | 0
2019-07-15 01:00 | 2 | 0 | 0.0342 | 0.0144 | 0.0005 | 0.054 | 0 | 0.1 | 0.0115 | 0.0023 | 0.04 | 0.039 | 0.003 | 0.067 | 0 | 0.001 | 0.1 | 0.006 | 0.011 | 0 | 0 | 0.0431 | 0 | 0.04 | 0.0236 | 0.215 | 0.0053 | 0.0001 | 0.025 | 0 | 0.058 | 0.0193 | 0.102 | 0.02 | 0 | 0.142 | 0.04 | 0 | 0 | 0.0076 | 0.0086 | 0.005 | 0.0141 | 0
2019-07-15 02:00 | 3 | 0 | 0.0308 | 0.0138 | 0.0004 | 0.058 | 0 | 0.1 | 0.0104 | 0.0022 | 0.04 | 0.037 | 0.004 | 0.065 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0431 | 0 | 0.04 | 0.0218 | 0.209 | 0.0048 | 0.0001 | 0.024 | 0 | 0.0539 | 0.018 | 0.106 | 0.02 | 0 | 0.153 | 0.04 | 0 | 0 | 0.0084 | 0.0083 | 0.005 | 0.0135 | 0
2019-07-15 03:00 | 4 | 0 | 0.0317 | 0.0137 | 0.0004 | 0.065 | 0 | 0.1 | 0.0099 | 0.0022 | 0.07 | 0.04 | 0.003 | 0.069 | 0 | 0.001 | 0.1 | 0 | 0.01 | 0.001 | 0 | 0.0401 | 0 | 0.07 | 0.0212 | 0.214 | 0.0046 | 0.0001 | 0.024 | 0 | 0.0509 | 0.0175 | 0.086 | 0.019 | 0 | 0.135 | 0.07 | 0 | 0 | 0.0074 | 0.0082 | 0.005 | 0.0144 | 0
2019-07-15 04:00 | 5 | 0 | 0.0347 | 0.0138 | 0.0004 | 0.062 | 0 | 0.25 | 0.0098 | 0.0021 | 0.07 | 0.039 | 0.003 | 0.077 | 0 | 0.001 | 0.25 | 0.001 | 0.011 | 0.001 | 0 | 0.0431 | 0 | 0.07 | 0.0211 | 0.204 | 0.0045 | 0.0001 | 0.025 | 0 | 0.0512 | 0.0174 | 0.09 | 0.028 | 0 | 0.127 | 0.07 | 0 | 0 | 0.0064 | 0.0082 | 0.005 | 0.0134 | 0
2019-07-15 05:00 | 6 | 0 | 0.0409 | 0.0144 | 0.0004 | 0.058 | 0 | 0.25 | 0.0099 | 0.0021 | 0.07 | 0.039 | 0.008 | 0.077 | 0 | 0.001 | 0.25 | 0.001 | 0.01 | 0.001 | 0 | 0.0631 | 0 | 0.07 | 0.0217 | 0.195 | 0.0046 | 0.0001 | 0.024 | 0 | 0.0511 | 0.018 | 0.087 | 0.047 | 0 | 0.123 | 0.07 | 0 | 0 | 0.0076 | 0.0073 | 0.005 | 0.015 | 0
2019-07-15 06:00 | 7 | 0 | 0.0364 | 0.0158 | 0.0004 | 0.051 | 0 | 0.25 | 0.0108 | 0.0022 | 0.07 | 0.036 | 0.009 | 0.087 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0 | 0 | 0.0631 | 0 | 0.07 | 0.0237 | 0.228 | 0.005 | 0.0001 | 0.028 | 0 | 0.0569 | 0.0197 | 0.084 | 0.101 | 0 | 0.123 | 0.07 | 0 | 0 | 0.0122 | 0.0296 | 0.005 | 0.0143 | 0
2019-07-15 07:00 | 8 | 0 | 0.0464 | 0.018 | 0.0005 | 0.054 | 0 | 0.25 | 0.0124 | 0.0024 | 0.11 | 0.037 | 0.011 | 0.097 | 0 | 0.001 | 0.25 | 0.001 | 0.017 | 0.001 | 0 | 0.1091 | 0 | 0.11 | 0.0271 | 0.246 | 0.0058 | 0.0001 | 0.032 | 0 | 0.0642 | 0.0225 | 0.083 | 0.113 | 0 | 0.105 | 0.11 | 0 | 0 | 0.01 | 0.0382 | 0.005 | 0.0182 | 0
2019-07-15 08:00 | 9 | 0 | 0.047 | 0.0194 | 0.0005 | 0.055 | 0 | 0.3 | 0.0137 | 0.0025 | 0.11 | 0.036 | 0.008 | 0.113 | 0 | 0.001 | 0.3 | 0 | 0.027 | 0.051 | 0 | 0.1551 | 0 | 0.11 | 0.0295 | 0.252 | 0.0063 | 0.0001 | 0.031 | 0 | 0.0713 | 0.0245 | 0.087 | 0.115 | 0 | 0.08 | 0.11 | 0 | 0 | 0.0086 | 0.0365 | 0.005 | 0.0185 | 0
2019-07-15 09:00 | 10 | 0 | 0.0479 | 0.0191 | 0.0005 | 0.058 | 0 | 0.3 | 0.0137 | 0.0025 | 0.11 | 0.036 | 0.005 | 0.111 | 0 | 0.001 | 0.3 | 0 | 0.02 | 0 | 0 | 0.1161 | 0 | 0.11 | 0.0294 | 0.244 | 0.0064 | 0.0001 | 0.038 | 0 | 0.0704 | 0.0244 | 0.056 | 0.105 | 0 | 0.018 | 0.11 | 0 | 0 | 0.0085 | 0.0355 | 0.005 | 0.0183 | 0
2019-07-15 10:00 | 11 | 0 | 0.0437 | 0.0187 | 0.0005 | 0.058 | 0 | 0.3 | 0.013 | 0.0025 | 0.11 | 0.034 | 0.003 | 0.108 | 0 | 0.001 | 0.3 | 0.014 | 0.015 | 0.006 | 0 | 0.1621 | 0 | 0.11 | 0.0283 | 0.253 | 0.0061 | 0.0001 | 0.037 | 0 | 0.0673 | 0.0236 | 0.047 | 0.107 | 0 | 0 | 0.11 | 0 | 0 | 0.0043 | 0.0333 | 0.005 | 0.0179 | 0
2019-07-15 11:00 | 12 | 0 | 0.0465 | 0.0184 | 0.0005 | 0.067 | 0 | 0.3 | 0.0126 | 0.0025 | 0.15 | 0.035 | 0 | 0.107 | 0 | 0.001 | 0.3 | 0.001 | 0.006 | 0.066 | 0 | 0.1331 | 0 | 0.15 | 0.0275 | 0.248 | 0.0059 | 0.0001 | 0.035 | 0 | 0.0661 | 0.023 | 0 | 0.098 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.0342 | 0.005 | 0.0165 | 0
2019-07-15 12:00 | 13 | 0 | 0.0403 | 0.018 | 0.0005 | 0.06 | 0 | 0.4 | 0.0121 | 0.0024 | 0.15 | 0.035 | 0 | 0.105 | 0 | 0.001 | 0.4 | 0.003 | 0.01 | 0.001 | 0 | 0.1521 | 0 | 0.15 | 0.0267 | 0.237 | 0.0056 | 0.0001 | 0.035 | 0 | 0.0628 | 0.0224 | 0 | 0.096 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0341 | 0.005 | 0.0172 | 0
2019-07-15 13:00 | 14 | 0 | 0.0399 | 0.0176 | 0.0004 | 0.056 | 0 | 0.4 | 0.0108 | 0.0023 | 0.15 | 0.034 | 0.002 | 0.12 | 0 | 0.001 | 0.4 | 0.004 | 0.013 | 0 | 0 | 0.1411 | 0 | 0.15 | 0.0248 | 0.228 | 0.005 | 0.0001 | 0.04 | 0 | 0.0579 | 0.021 | 0 | 0.099 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0379 | 0.005 | 0.0178 | 0
2019-07-15 14:00 | 15 | 0 | 0.0407 | 0.0174 | 0.0004 | 0.064 | 0 | 0.5 | 0.0103 | 0.0023 | 0.15 | 0.035 | 0 | 0.108 | 0 | 0.001 | 0.5 | 0.001 | 0.01 | 0 | 0 | 0.1731 | 0 | 0.15 | 0.0242 | 0.216 | 0.0048 | 0.0001 | 0.04 | 0 | 0.055 | 0.0205 | 0 | 0.096 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0388 | 0.005 | 0.0186 | 0
2019-07-15 15:00 | 16 | 0 | 0.0388 | 0.0175 | 0.0004 | 0.052 | 0 | 0.55 | 0.0105 | 0.0024 | 0.15 | 0.035 | 0 | 0.104 | 0 | 0.001 | 0.55 | 0.001 | 0.011 | 0 | 0 | 0.1361 | 0 | 0.15 | 0.0245 | 0.218 | 0.0049 | 0.0001 | 0.033 | 0 | 0.0568 | 0.0207 | 0.001 | 0.09 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0388 | 0.005 | 0.0177 | 0
2019-07-15 16:00 | 17 | 0 | 0.0405 | 0.0187 | 0.0005 | 0.05 | 0 | 0.629 | 0.0123 | 0.0024 | 0.23 | 0.037 | 0 | 0.112 | 0 | 0.001 | 0.593 | 0 | 0.008 | 0.001 | 0 | 0.1381 | 0 | 0.278 | 0.0274 | 0.216 | 0.0057 | 0.0001 | 0.032 | 0 | 0.0642 | 0.023 | 0 | 0.08 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0362 | 0.005 | 0.0178 | 0
2019-07-15 17:00 | 18 | 0 | 0.0398 | 0.0202 | 0.0007 | 0.058 | 0 | 0.629 | 0.0167 | 0.0027 | 0.23 | 0.009 | 0 | 0.11 | 0 | 0.001 | 0.593 | 0.019 | 0.009 | 0 | 0 | 0.1962 | 0 | 0.278 | 0.0337 | 0.221 | 0.0077 | 0.0001 | 0.031 | 0 | 0.0849 | 0.0277 | 0 | 0.075 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0161 | 0.005 | 0.0184 | 0
2019-07-15 18:00 | 19 | 0 | 0.0396 | 0.0209 | 0.0008 | 0.052 | 0 | 0.52 | 0.0192 | 0.0029 | 0.16 | 0.008 | 0 | 0.108 | 0 | 0.001 | 0.52 | 0 | 0.01 | 0.001 | 0 | 0.1242 | 0 | 0.16 | 0.0372 | 0.239 | 0.0088 | 0.0002 | 0.032 | 0 | 0.0951 | 0.0303 | 0.032 | 0.02 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0096 | 0.005 | 0.0211 | 0
2019-07-15 19:00 | 20 | 0 | 0.0407 | 0.0213 | 0.0008 | 0.049 | 0 | 0.5 | 0.0194 | 0.003 | 0.17 | 0.005 | 0 | 0.103 | 0 | 0.001 | 0.5 | 0.001 | 0.019 | 0.066 | 0 | 0.1162 | 0 | 0.17 | 0.0377 | 0.25 | 0.0089 | 0.0002 | 0.034 | 0 | 0.096 | 0.0306 | 0.071 | 0.017 | 0 | 0.041 | 0.123 | 0 | 0 | 0.0033 | 0.0096 | 0.005 | 0.0204 | 0
2019-07-15 20:00 | 21 | 0 | 0.0324 | 0.0205 | 0.0008 | 0.056 | 0 | 0.3 | 0.019 | 0.0029 | 0.11 | 0.006 | 0 | 0.095 | 0 | 0.001 | 0.3 | 0.001 | 0.017 | 0.098 | 0 | 0.1162 | 0 | 0.11 | 0.0367 | 0.235 | 0.0088 | 0.0002 | 0.035 | 0 | 0.095 | 0.0298 | 0.086 | 0.016 | 0 | 0.116 | 0.11 | 0 | 0 | 0.007 | 0.0085 | 0.005 | 0.0197 | 0
2019-07-15 21:00 | 22 | 0 | 0.0371 | 0.0197 | 0.0008 | 0.052 | 0 | 0.31 | 0.0186 | 0.0028 | 0.09 | 0.051 | 0.004 | 0.088 | 0 | 0.001 | 0.31 | 0 | 0.014 | 0.001 | 0 | 0.1262 | 0 | 0.09 | 0.0357 | 0.233 | 0.0086 | 0.0002 | 0.031 | 0 | 0.0917 | 0.0289 | 0.108 | 0.015 | 0 | 0.138 | 0.06 | 0 | 0 | 0.0077 | 0.0093 | 0.005 | 0.0191 | 0
2019-07-15 22:00 | 23 | 0 | 0.0352 | 0.0193 | 0.0008 | 0.065 | 0 | 0.2 | 0.0193 | 0.0028 | 0.09 | 0.051 | 0.005 | 0.09 | 0 | 0.001 | 0.2 | 0.001 | 0.013 | 0.012 | 0 | 0.1052 | 0 | 0.09 | 0.0363 | 0.233 | 0.0089 | 0.0002 | 0.034 | 0 | 0.0956 | 0.0293 | 0.118 | 0.017 | 0 | 0.145 | 0.03 | 0 | 0 | 0.0106 | 0.0104 | 0.005 | 0.0188 | 0
2019-07-15 23:00 | 24 | 0 | 0.0355 | 0.0181 | 0.0008 | 0.066 | 0 | 0.1 | 0.0177 | 0.0027 | 0.05 | 0.051 | 0.005 | 0.113 | 0 | 0.001 | 0.1 | 0 | 0.014 | 0.001 | 0 | 0.0722 | 0 | 0.05 | 0.0335 | 0.229 | 0.0081 | 0.0001 | 0.031 | 0 | 0.0879 | 0.027 | 0.11 | 0.015 | 0 | 0.148 | 0.04 | 0 | 0 | 0.0091 | 0.01 | 0.005 | 0.0186 | 0
2019-07-16 | 25 | 0 | 0.0353 | 0.0162 | 0.0006 | 0.065 | 0 | 0.1 | 0.0141 | 0.0025 | 0.04 | 0.052 | 0.004 | 0.1 | 0 | 0.001 | 0.1 | 0 | 0.012 | 0.001 | 0 | 0.0862 | 0 | 0.04 | 0.0279 | 0.229 | 0.0065 | 0.0001 | 0.034 | 0 | 0.0703 | 0.0228 | 0.113 | 0.016 | 0 | 0.139 | 0.04 | 0 | 0 | 0.0084 | 0.0082 | 0.005 | 0.0168 | 0
2019-07-16 01:00 | 26 | 0 | 0.0335 | 0.0151 | 0.0005 | 0.068 | 0 | 0.1 | 0.012 | 0.0023 | 0.04 | 0.051 | 0.003 | 0.098 | 0 | 0.001 | 0.1 | 0.001 | 0.01 | 0 | 0 | 0.0411 | 0 | 0.04 | 0.0246 | 0.216 | 0.0055 | 0.0001 | 0.03 | 0 | 0.0604 | 0.0202 | 0.108 | 0.021 | 0 | 0.151 | 0.04 | 0 | 0 | 0.0079 | 0.0087 | 0.005 | 0.0157 | 0
2019-07-16 02:00 | 27 | 0 | 0.0362 | 0.0147 | 0.0004 | 0.063 | 0 | 0.1 | 0.0109 | 0.0022 | 0.04 | 0.052 | 0.004 | 0.085 | 0 | 0.001 | 0.1 | 0 | 0.011 | 0.001 | 0 | 0.0411 | 0 | 0.04 | 0.023 | 0.207 | 0.005 | 0.0001 | 0.032 | 0 | 0.0564 | 0.0189 | 0.092 | 0.018 | 0 | 0.152 | 0.04 | 0 | 0 | 0.0087 | 0.0085 | 0.005 | 0.0143 | 0
2019-07-16 03:00 | 28 | 0 | 0.03 | 0.0145 | 0.0004 | 0.064 | 0 | 0.1 | 0.0103 | 0.0021 | 0.07 | 0.051 | 0.003 | 0.088 | 0 | 0.001 | 0.1 | 0.001 | 0.01 | 0.001 | 0 | 0.0401 | 0 | 0.07 | 0.0222 | 0.207 | 0.0048 | 0.0001 | 0.03 | 0 | 0.0529 | 0.0184 | 0.098 | 0.019 | 0 | 0.139 | 0.07 | 0 | 0 | 0.0077 | 0.0084 | 0.005 | 0.0141 | 0.013
2019-07-16 04:00 | 29 | 0 | 0.0329 | 0.0142 | 0.0004 | 0.07 | 0 | 0.25 | 0.0101 | 0.002 | 0.07 | 0.052 | 0.004 | 0.085 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0.001 | 0 | 0.0461 | 0 | 0.07 | 0.0217 | 0.209 | 0.0047 | 0.0001 | 0.031 | 0 | 0.0527 | 0.0179 | 0.107 | 0.028 | 0 | 0.133 | 0.07 | 0 | 0 | 0.0086 | 0.0083 | 0.005 | 0.0148 | 0
2019-07-16 05:00 | 30 | 0 | 0.0469 | 0.0145 | 0.0004 | 0.057 | 0 | 0.25 | 0.01 | 0.0021 | 0.07 | 0.051 | 0.007 | 0.075 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0.001 | 0 | 0.0661 | 0 | 0.07 | 0.0219 | 0.219 | 0.0047 | 0.0001 | 0.032 | 0 | 0.0517 | 0.0181 | 0.094 | 0.036 | 0 | 0.127 | 0.07 | 0 | 0 | 0.0077 | 0.0074 | 0.005 | 0.0151 | 0
2019-07-16 06:00 | 31 | 0 | 0.0404 | 0.0156 | 0.0004 | 0.053 | 0 | 0.25 | 0.0109 | 0.0022 | 0.07 | 0.049 | 0.011 | 0.087 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0 | 0 | 0.0831 | 0 | 0.07 | 0.0237 | 0.231 | 0.0051 | 0.0001 | 0.033 | 0 | 0.0573 | 0.0196 | 0.08 | 0.093 | 0 | 0.123 | 0.07 | 0 | 0 | 0.0081 | 0.0196 | 0.005 | 0.014 | 0.006
2019-07-16 07:00 | 32 | 0 | 0.0453 | 0.0177 | 0.0005 | 0.055 | 0 | 0.25 | 0.0124 | 0.0023 | 0.11 | 0.052 | 0.011 | 0.103 | 0 | 0.001 | 0.25 | 0 | 0.015 | 0.001 | 0 | 0.1291 | 0 | 0.11 | 0.0269 | 0.253 | 0.0058 | 0.0001 | 0.039 | 0 | 0.064 | 0.0223 | 0.092 | 0.105 | 0 | 0.099 | 0.11 | 0 | 0 | 0.0099 | 0.0311 | 0.005 | 0.017 | 0
2019-07-16 08:00 | 33 | 0 | 0.0429 | 0.0194 | 0.0005 | 0.054 | 0 | 0.3 | 0.0134 | 0.0022 | 0.11 | 0.05 | 0.009 | 0.114 | 0 | 0.001 | 0.3 | 0.001 | 0.022 | 0 | 0 | 0.1311 | 0 | 0.11 | 0.0293 | 0.038 | 0.0063 | 0.0001 | 0.038 | 0 | 0.0704 | 0.0243 | 0.085 | 0.101 | 0 | 0.074 | 0.11 | 0 | 0 | 0.0096 | 0.0395 | 0.005 | 0.0185 | 0.009
2019-07-16 09:00 | 34 | 0 | 0.044 | 0.0196 | 0.0005 | 0.054 | 0 | 0.3 | 0.0134 | 0.0022 | 0.11 | 0.049 | 0.004 | 0.122 | 0 | 0.001 | 0.3 | 0.001 | 0.02 | 0.024 | 0 | 0.1261 | 0 | 0.11 | 0.0293 | 0.001 | 0.0062 | 0.0001 | 0.034 | 0 | 0.0692 | 0.0244 | 0.072 | 0.092 | 0 | 0.026 | 0.11 | 0 | 0 | 0.0067 | 0.0355 | 0.005 | 0.0186 | 0
2019-07-16 10:00 | 35 | 0 | 0.0395 | 0.019 | 0.0005 | 0.05 | 0 | 0.3 | 0.0121 | 0.0022 | 0.11 | 0.05 | 0.005 | 0.127 | 0 | 0.001 | 0.3 | 0.004 | 0.013 | 0 | 0 | 0.1161 | 0 | 0.11 | 0.0274 | 0.002 | 0.0056 | 0.0001 | 0.036 | 0 | 0.0634 | 0.023 | 0.074 | 0.105 | 0 | 0.022 | 0.11 | 0 | 0 | 0.0064 | 0.0332 | 0.005 | 0.0181 | 0
2019-07-16 11:00 | 36 | 0 | 0.0402 | 0.0187 | 0.0004 | 0.052 | 0 | 0.3 | 0.0111 | 0.0022 | 0.15 | 0.048 | 0 | 0.12 | 0 | 0.001 | 0.3 | 0.003 | 0.012 | 0 | 0 | 0.1281 | 0 | 0.15 | 0.026 | 0.001 | 0.0052 | 0.0001 | 0.041 | 0 | 0.0601 | 0.022 | 0.041 | 0.099 | 0 | 0 | 0.13 | 0 | 0 | 0.0003 | 0.0341 | 0.005 | 0.0177 | 0
2019-07-16 12:00 | 37 | 0 | 0.041 | 0.018 | 0.0004 | 0.054 | 0 | 0.4 | 0.0107 | 0.0021 | 0.15 | 0.049 | 0 | 0.114 | 0 | 0.001 | 0.4 | 0.001 | 0.012 | 0.019 | 0 | 0.1271 | 0 | 0.15 | 0.0251 | 0.074 | 0.005 | 0.0001 | 0.041 | 0 | 0.0571 | 0.0213 | 0.009 | 0.091 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0329 | 0.005 | 0.0171 | 0.044
2019-07-16 13:00 | 38 | 0 | 0.0399 | 0.0179 | 0.0004 | 0.054 | 0 | 0.4 | 0.0104 | 0.0021 | 0.15 | 0.049 | 0 | 0.115 | 0 | 0.001 | 0.4 | 0.001 | 0.013 | 0.014 | 0 | 0.1401 | 0 | 0.15 | 0.0246 | 0.226 | 0.0049 | 0.0001 | 0.039 | 0 | 0.0566 | 0.0209 | 0 | 0.094 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0338 | 0.005 | 0.018 | 0.025
2019-07-16 14:00 | 39 | 0 | 0.042 | 0.0182 | 0.0004 | 0.051 | 0 | 0.5 | 0.0106 | 0.002 | 0.15 | 0.048 | 0 | 0.101 | 0 | 0.001 | 0.5 | 0.001 | 0.008 | 0.025 | 0 | 0.1091 | 0 | 0.15 | 0.025 | 0.216 | 0.005 | 0.0001 | 0.039 | 0 | 0.0566 | 0.0212 | 0 | 0.099 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0339 | 0.005 | 0.0173 | 0
2019-07-16 15:00 | 40 | 0 | 0.04 | 0.0181 | 0.0004 | 0.052 | 0 | 0.55 | 0.0107 | 0.0021 | 0.15 | 0.049 | 0 | 0.109 | 0 | 0.001 | 0.55 | 0.003 | 0.011 | 0 | 0 | 0.1071 | 0 | 0.15 | 0.0251 | 0.203 | 0.005 | 0.0001 | 0.037 | 0 | 0.0579 | 0.0213 | 0 | 0.092 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0329 | 0.005 | 0.0172 | 0.023
2019-07-16 16:00 | 41 | 0 | 0.0396 | 0.0191 | 0.0005 | 0.051 | 0 | 0.629 | 0.0121 | 0.0022 | 0.23 | 0.011 | 0 | 0.139 | 0 | 0.001 | 0.593 | 0.001 | 0.006 | 0.011 | 0 | 0.1061 | 0 | 0.278 | 0.0274 | 0.203 | 0.0057 | 0.0001 | 0.038 | 0 | 0.0636 | 0.0231 | 0 | 0.087 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0343 | 0.005 | 0.0191 | 0.034
2019-07-16 17:00 | 42 | 0 | 0.0429 | 0.0206 | 0.0007 | 0.046 | 0 | 0.629 | 0.0165 | 0.0026 | 0.23 | 0.009 | 0 | 0.138 | 0 | 0.001 | 0.593 | 0.001 | 0.014 | 0.011 | 0 | 0.1092 | 0 | 0.278 | 0.0338 | 0.21 | 0.0076 | 0.0001 | 0.029 | 0 | 0.0845 | 0.0279 | 0.023 | 0.082 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0261 | 0.005 | 0.0187 | 0.05
2019-07-16 18:00 | 43 | 0 | 0.0394 | 0.0206 | 0.0008 | 0.05 | 0 | 0.52 | 0.0188 | 0.0029 | 0.16 | 0.006 | 0 | 0.123 | 0 | 0.001 | 0.52 | 0.001 | 0.018 | 0 | 0 | 0.1162 | 0 | 0.16 | 0.0366 | 0.228 | 0.0087 | 0.0002 | 0.033 | 0 | 0.0932 | 0.0297 | 0.028 | 0.027 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0235 | 0.005 | 0.0208 | 0.053
2019-07-16 19:00 | 44 | 0 | 0.0396 | 0.0209 | 0.0008 | 0.052 | 0 | 0.5 | 0.0194 | 0.0029 | 0.17 | 0.005 | 0 | 0.119 | 0 | 0.001 | 0.5 | 0 | 0.018 | 0.01 | 0 | 0.1042 | 0 | 0.17 | 0.0375 | 0.245 | 0.0089 | 0.0002 | 0.035 | 0 | 0.0958 | 0.0304 | 0.033 | 0.024 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0216 | 0.005 | 0.0201 | 0.051
2019-07-16 20:00 | 45 | 0 | 0.0324 | 0.0204 | 0.0008 | 0.053 | 0 | 0.3 | 0.0189 | 0.0029 | 0.11 | 0.01 | 0 | 0.114 | 0 | 0.001 | 0.3 | 0 | 0.016 | 0 | 0 | 0.1042 | 0 | 0.11 | 0.0365 | 0.227 | 0.0087 | 0.0002 | 0.028 | 0 | 0.0944 | 0.0296 | 0.073 | 0.023 | 0 | 0.07 | 0.11 | 0 | 0 | 0.005 | 0.0185 | 0.005 | 0.0187 | 0.051
2019-07-16 21:00 | 46 | 0 | 0.033 | 0.0195 | 0.0008 | 0.053 | 0 | 0.31 | 0.0181 | 0.0028 | 0.09 | 0.052 | 0.003 | 0.107 | 0 | 0.001 | 0.31 | 0.001 | 0.01 | 0.001 | 0 | 0.0932 | 0 | 0.09 | 0.035 | 0.226 | 0.0084 | 0.0001 | 0.031 | 0 | 0.0896 | 0.0284 | 0.102 | 0.023 | 0 | 0.14 | 0.06 | 0 | 0 | 0.0076 | 0.0162 | 0.005 | 0.0198 | 0.05
2019-07-16 22:00 | 47 | 0 | 0.0351 | 0.0191 | 0.0008 | 0.063 | 0 | 0.2 | 0.0193 | 0.0028 | 0.09 | 0.05 | 0.005 | 0.099 | 0 | 0.001 | 0.2 | 0.001 | 0.009 | 0.013 | 0 | 0.0602 | 0 | 0.09 | 0.0361 | 0.234 | 0.0088 | 0.0002 | 0.031 | 0 | 0.0952 | 0.0291 | 0.113 | 0.024 | 0 | 0.16 | 0.03 | 0 | 0 | 0.0095 | 0.0164 | 0.005 | 0.0186 | 0.05
2019-07-16 23:00 | 48 | 0 | 0.0335 | 0.0178 | 0.0008 | 0.064 | 0 | 0.1 | 0.018 | 0.0026 | 0.05 | 0.051 | 0.004 | 0.126 | 0 | 0.001 | 0.1 | 0.001 | 0.01 | 0.001 | 0 | 0.0472 | 0 | 0.05 | 0.0337 | 0.229 | 0.0083 | 0.0002 | 0.032 | 0 | 0.0889 | 0.0271 | 0.112 | 0.023 | 0 | 0.16 | 0.04 | 0 | 0 | 0.01 | 0.015 | 0.005 | 0.0184 | 0.051
2019-07-17 | 49 | 0 | 0.0343 | 0.0159 | 0.0006 | 0.063 | 0 | 0.1 | 0.0145 | 0.0023 | 0.04 | 0.052 | 0.005 | 0.111 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0552 | 0 | 0.04 | 0.0282 | 0.23 | 0.0067 | 0.0001 | 0.031 | 0 | 0.0717 | 0.0229 | 0.115 | 0.02 | 0 | 0.15 | 0.04 | 0 | 0 | 0.0082 | 0.0122 | 0.005 | 0.0156 | 0
2019-07-17 01:00 | 50 | 0 | 0.0325 | 0.0149 | 0.0005 | 0.059 | 0 | 0.1 | 0.0122 | 0.0021 | 0.04 | 0.052 | 0.004 | 0.112 | 0 | 0.001 | 0.1 | 0 | 0.008 | 0.001 | 0 | 0.0381 | 0 | 0.04 | 0.0248 | 0.217 | 0.0057 | 0.0001 | 0.03 | 0 | 0.0615 | 0.0203 | 0.104 | 0.024 | 0 | 0.145 | 0.04 | 0 | 0 | 0.0078 | 0.0097 | 0.005 | 0.0155 | 0
2019-07-17 02:00 | 51 | 0 | 0.0322 | 0.0146 | 0.0004 | 0.057 | 0 | 0.1 | 0.011 | 0.0021 | 0.04 | 0.051 | 0.005 | 0.093 | 0 | 0.001 | 0.1 | 0.001 | 0.008 | 0.001 | 0 | 0.0421 | 0 | 0.04 | 0.0231 | 0.211 | 0.0051 | 0.0001 | 0.031 | 0 | 0.0569 | 0.019 | 0.098 | 0.023 | 0 | 0.138 | 0.04 | 0 | 0 | 0.0077 | 0.0095 | 0.005 | 0.0142 | 0
2019-07-17 03:00 | 52 | 0 | 0.033 | 0.0144 | 0.0004 | 0.068 | 0 | 0.1 | 0.0104 | 0.0021 | 0.07 | 0.053 | 0.004 | 0.092 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0431 | 0 | 0.07 | 0.0222 | 0.21 | 0.0048 | 0.0001 | 0.035 | 0 | 0.0531 | 0.0183 | 0.096 | 0.021 | 0 | 0.131 | 0.07 | 0 | 0 | 0.0076 | 0.0094 | 0.005 | 0.014 | 0
2019-07-17 04:00 | 53 | 0 | 0.0318 | 0.0139 | 0.0004 | 0.054 | 0 | 0.25 | 0.0101 | 0.002 | 0.07 | 0.055 | 0.004 | 0.093 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0.001 | 0 | 0.0461 | 0 | 0.07 | 0.0215 | 0.213 | 0.0047 | 0.0001 | 0.03 | 0 | 0.0526 | 0.0178 | 0.109 | 0.029 | 0 | 0.125 | 0.07 | 0 | 0 | 0.0075 | 0.0083 | 0.005 | 0.0146 | 0.054
2019-07-17 05:00 | 54 | 0 | 0.041 | 0.0145 | 0.0004 | 0.061 | 0 | 0.25 | 0.0102 | 0.0021 | 0.07 | 0.053 | 0.008 | 0.079 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0 | 0 | 0.0641 | 0 | 0.07 | 0.0221 | 0.223 | 0.0048 | 0.0001 | 0.031 | 0 | 0.0526 | 0.0183 | 0.081 | 0.053 | 0 | 0.119 | 0.07 | 0 | 0 | 0.0067 | 0.0084 | 0.005 | 0.0141 | 0.053
2019-07-17 06:00 | 55 | 0 | 0.0356 | 0.0161 | 0.0004 | 0.055 | 0 | 0.25 | 0.0111 | 0.0023 | 0.07 | 0.051 | 0.009 | 0.091 | 0 | 0.001 | 0.25 | 0 | 0.008 | 0 | 0 | 0.0571 | 0 | 0.07 | 0.0242 | 0.23 | 0.0051 | 0.0001 | 0.031 | 0 | 0.0581 | 0.02 | 0.078 | 0.109 | 0 | 0.105 | 0.07 | 0 | 0 | 0.0083 | 0.0187 | 0.005 | 0.0165 | 0.05
2019-07-17 07:00 | 56 | 0 | 0.0406 | 0.0186 | 0.0005 | 0.051 | 0 | 0.25 | 0.0129 | 0.0026 | 0.11 | 0.053 | 0.004 | 0.093 | 0 | 0.001 | 0.25 | 0 | 0.008 | 0.001 | 0 | 0.1171 | 0 | 0.11 | 0.0281 | 0.256 | 0.006 | 0.0001 | 0.032 | 0 | 0.0665 | 0.0233 | 0.073 | 0.124 | 0 | 0.059 | 0.11 | 0 | 0 | 0.0103 | 0.0303 | 0.005 | 0.0198 | 0.051
2019-07-17 08:00 | 57 | 0 | 0.0394 | 0.0205 | 0.0006 | 0.056 | 0 | 0.3 | 0.0142 | 0.0029 | 0.11 | 0.051 | 0 | 0.104 | 0 | 0.001 | 0.3 | 0.001 | 0.014 | 0.022 | 0 | 0.1132 | 0 | 0.11 | 0.0309 | 0.265 | 0.0066 | 0.0001 | 0.039 | 0 | 0.0743 | 0.0257 | 0.031 | 0.119 | 0 | 0 | 0.11 | 0 | 0 | 0.001 | 0.0337 | 0.005 | 0.0194 | 0.051
2019-07-17 09:00 | 58 | 0 | 0.0444 | 0.0205 | 0.0005 | 0.053 | 0 | 0.3 | 0.0141 | 0.0029 | 0.11 | 0.049 | 0 | 0.102 | 0 | 0.001 | 0.3 | 0.001 | 0.006 | 0 | 0 | 0.1192 | 0 | 0.11 | 0.0309 | 0.259 | 0.0066 | 0.0001 | 0.039 | 0 | 0.0731 | 0.0257 | 0 | 0.096 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0347 | 0.005 | 0.0195 | 0.05
2019-07-17 10:00 | 59 | 0 | 0.0418 | 0.0197 | 0.0005 | 0.055 | 0 | 0.3 | 0.0127 | 0.0028 | 0.11 | 0.05 | 0 | 0.11 | 0 | 0.001 | 0.3 | 0.001 | 0 | 0.003 | 0 | 0.1351 | 0 | 0.11 | 0.0286 | 0.26 | 0.0059 | 0.0001 | 0.036 | 0 | 0.0665 | 0.024 | 0 | 0.106 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0384 | 0.005 | 0.0187 | 0.051
2019-07-17 11:00 | 60 | 0 | 0.0398 | 0.0198 | 0.0005 | 0.06 | 0 | 0.3 | 0.0122 | 0.0027 | 0.15 | 0.051 | 0 | 0.122 | 0 | 0.001 | 0.3 | 0 | 0 | 0.002 | 0 | 0.1141 | 0 | 0.15 | 0.028 | 0.244 | 0.0057 | 0.0001 | 0.038 | 0 | 0.0655 | 0.0237 | 0 | 0.116 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.0364 | 0.005 | 0.0197 | 0.05
2019-07-17 12:00 | 61 | 0 | 0.0454 | 0.0188 | 0.0004 | 0.058 | 0 | 0.4 | 0.0117 | 0.0026 | 0.15 | 0.054 | 0 | 0.105 | 0 | 0.001 | 0.4 | 0.004 | 0 | 0 | 0 | 0.1461 | 0 | 0.15 | 0.0268 | 0.236 | 0.0055 | 0.0001 | 0.035 | 0 | 0.0618 | 0.0226 | 0 | 0.108 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0382 | 0.005 | 0.0179 | 0.051
2019-07-17 13:00 | 62 | 0 | 0.0442 | 0.0186 | 0.0004 | 0.059 | 0 | 0.4 | 0.0111 | 0.0026 | 0.15 | 0.051 | 0 | 0.114 | 0 | 0.001 | 0.4 | 0.007 | 0 | 0 | 0 | 0.1891 | 0 | 0.15 | 0.0259 | 0.227 | 0.0052 | 0.0001 | 0.037 | 0 | 0.0601 | 0.022 | 0 | 0.115 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.038 | 0.005 | 0.0176 | 0.051
2019-07-17 14:00 | 63 | 0 | 0.0451 | 0.0184 | 0.0004 | 0.057 | 0 | 0.5 | 0.011 | 0.0025 | 0.15 | 0.05 | 0 | 0.111 | 0 | 0.001 | 0.5 | 0.008 | 0 | 0.042 | 0 | 0.1351 | 0 | 0.15 | 0.0256 | 0.223 | 0.0052 | 0.0001 | 0.039 | 0 | 0.0584 | 0.0217 | 0 | 0.114 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.037 | 0.005 | 0.0185 | 0.05
2019-07-17 15:00 | 64 | 0 | 0.0451 | 0.0183 | 0.0004 | 0.056 | 0 | 0.55 | 0.0109 | 0.0025 | 0.15 | 0.053 | 0 | 0.114 | 0 | 0.001 | 0.55 | 0.012 | 0 | 0.087 | 0 | 0.1481 | 0 | 0.15 | 0.0255 | 0.223 | 0.0051 | 0.0001 | 0.035 | 0 | 0.0591 | 0.0216 | 0 | 0.103 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.04 | 0.005 | 0.0174 | 0.048
2019-07-17 16:00 | 65 | 0 | 0.0428 | 0.0194 | 0.0005 | 0.054 | 0 | 0.629 | 0.0129 | 0.0027 | 0.23 | 0.053 | 0 | 0.131 | 0 | 0.001 | 0.593 | 0.002 | 0.002 | 0.007 | 0 | 0.1341 | 0 | 0.278 | 0.0287 | 0.21 | 0.006 | 0.0001 | 0.035 | 0 | 0.0674 | 0.0241 | 0 | 0.096 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0404 | 0.005 | 0.0185 | 0.052
2019-07-17 17:00 | 66 | 0 | 0.0453 | 0.0211 | 0.0007 | 0.053 | 0 | 0.629 | 0.0175 | 0.0031 | 0.23 | 0.051 | 0 | 0.124 | 0 | 0.001 | 0.593 | 0.025 | 0.014 | 0.014 | 0 | 0.1282 | 0 | 0.278 | 0.0353 | 0.211 | 0.0081 | 0.0001 | 0.039 | 0 | 0.0889 | 0.029 | 0 | 0.085 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0353 | 0.005 | 0.0192 | 0.053
2019-07-17 18:00 | 67 | 0 | 0.0397 | 0.0212 | 0.0008 | 0.056 | 0 | 0.52 | 0.0192 | 0.0032 | 0.16 | 0.051 | 0 | 0.123 | 0 | 0.001 | 0.52 | 0.002 | 0.017 | 0 | 0 | 0.1502 | 0 | 0.16 | 0.0375 | 0.223 | 0.0089 | 0.0002 | 0.038 | 0 | 0.0955 | 0.0305 | 0.054 | 0.025 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0246 | 0.005 | 0.0224 | 0.05
2019-07-17 19:00 | 68 | 0 | 0.0408 | 0.0218 | 0.0008 | 0.053 | 0 | 0.5 | 0.019 | 0.0032 | 0.17 | 0.051 | 0 | 0.114 | 0 | 0.001 | 0.5 | 0.008 | 0.022 | 0 | 0 | 0.1382 | 0 | 0.17 | 0.0377 | 0.235 | 0.0088 | 0.0002 | 0.034 | 0 | 0.095 | 0.0307 | 0.064 | 0.022 | 0 | 0 | 0.123 | 0 | 0 | 0.0015 | 0.0087 | 0.005 | 0.0209 | 0.051
2019-07-17 20:00 | 69 | 0 | 0.0365 | 0.0209 | 0.0008 | 0.052 | 0 | 0.3 | 0.0187 | 0.0031 | 0.11 | 0.052 | 0 | 0.112 | 0 | 0.001 | 0.3 | 0.008 | 0.019 | 0.007 | 0 | 0.1232 | 0 | 0.11 | 0.0367 | 0.219 | 0.0086 | 0.0002 | 0.03 | 0 | 0.094 | 0.0298 | 0.09 | 0.023 | 0 | 0.078 | 0.11 | 0 | 0 | 0.0062 | 0.0085 | 0.005 | 0.0201 | 0.052
2019-07-17 21:00 | 70 | 0 | 0.0393 | 0.0203 | 0.0008 | 0.053 | 0 | 0.31 | 0.0185 | 0.0031 | 0.09 | 0.054 | 0.004 | 0.106 | 0 | 0.001 | 0.31 | 0.005 | 0.014 | 0.029 | 0 | 0.1412 | 0 | 0.09 | 0.036 | 0.216 | 0.0085 | 0.0002 | 0.034 | 0 | 0.0917 | 0.0292 | 0.107 | 0.018 | 0 | 0.14 | 0.06 | 0 | 0 | 0.0089 | 0.0094 | 0.005 | 0.0195 | 0.05
2019-07-17 22:00 | 71 | 0 | 0.0382 | 0.0196 | 0.0008 | 0.067 | 0 | 0.2 | 0.0191 | 0.003 | 0.09 | 0.055 | 0.005 | 0.093 | 0 | 0.001 | 0.2 | 0.001 | 0.009 | 0.01 | 0 | 0.0812 | 0 | 0.09 | 0.0363 | 0.222 | 0.0088 | 0.0002 | 0.036 | 0 | 0.095 | 0.0293 | 0.114 | 0.018 | 0 | 0.147 | 0.03 | 0 | 0 | 0.0097 | 0.0094 | 0.005 | 0.019 | 0.053
2019-07-17 23:00 | 72 | 0 | 0.0354 | 0.018 | 0.0007 | 0.063 | 0 | 0.1 | 0.0174 | 0.0028 | 0.05 | 0.053 | 0.004 | 0.091 | 0 | 0.001 | 0.1 | 0.002 | 0.009 | 0.044 | 0 | 0.0522 | 0 | 0.05 | 0.0331 | 0.229 | 0.008 | 0.0001 | 0.036 | 0 | 0.0864 | 0.0267 | 0.11 | 0.02 | 0 | 0.142 | 0.04 | 0 | 0 | 0.0101 | 0.0129 | 0.005 | 0.0175 | 0.053
2019-07-18 | 73 | 0 | 0.0362 | 0.016 | 0.0006 | 0.065 | 0 | 0.1 | 0.0143 | 0.0024 | 0.04 | 0.053 | 0.005 | 0.083 | 0 | 0.001 | 0.1 | 0.01 | 0.01 | 0.001 | 0 | 0.0412 | 0 | 0.04 | 0.028 | 0.226 | 0.0066 | 0.0001 | 0.028 | 0 | 0.071 | 0.0228 | 0.114 | 0.017 | 0 | 0.135 | 0.04 | 0 | 0 | 0.0083 | 0.0142 | 0.005 | 0.0156 | 0
2019-07-18 01:00 | 74 | 0 | 0.0356 | 0.0151 | 0.0005 | 0.063 | 0 | 0.1 | 0.0123 | 0.0022 | 0.04 | 0.054 | 0.004 | 0.085 | 0 | 0.001 | 0.1 | 0.001 | 0.009 | 0.001 | 0 | 0.0411 | 0 | 0.04 | 0.025 | 0.217 | 0.0057 | 0.0001 | 0.031 | 0 | 0.0617 | 0.0204 | 0.102 | 0.02 | 0 | 0.142 | 0.04 | 0 | 0 | 0.0079 | 0.0088 | 0.005 | 0.0157 | 0
2019-07-18 02:00 | 75 | 0 | 0.0352 | 0.0146 | 0.0004 | 0.059 | 0 | 0.1 | 0.0111 | 0.0022 | 0.04 | 0.054 | 0.005 | 0.075 | 0 | 0.001 | 0.1 | 0 | 0.008 | 0.001 | 0 | 0.0421 | 0 | 0.04 | 0.0233 | 0.216 | 0.0051 | 0.0001 | 0.028 | 0 | 0.0574 | 0.0191 | 0.103 | 0.021 | 0 | 0.136 | 0.04 | 0 | 0 | 0.0077 | 0.0085 | 0.005 | 0.0143 | 0
2019-07-18 03:00 | 76 | 0 | 0.036 | 0.0144 | 0.0004 | 0.06 | 0 | 0.1 | 0.0104 | 0.0022 | 0.07 | 0.056 | 0.004 | 0.076 | 0 | 0.001 | 0.1 | 0.001 | 0.009 | 0.001 | 0 | 0.0391 | 0 | 0.07 | 0.0223 | 0.214 | 0.0048 | 0.0001 | 0.03 | 0 | 0.0533 | 0.0184 | 0.096 | 0.021 | 0 | 0.129 | 0.07 | 0 | 0 | 0.0076 | 0.0084 | 0.005 | 0.014 | 0
2019-07-18 04:00 | 77 | 0 | 0.0349 | 0.0142 | 0.0004 | 0.063 | 0 | 0.25 | 0.0102 | 0.0021 | 0.07 | 0.055 | 0.005 | 0.074 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0 | 0 | 0.0511 | 0 | 0.07 | 0.0219 | 0.195 | 0.0047 | 0.0001 | 0.029 | 0 | 0.0533 | 0.0181 | 0.107 | 0.023 | 0 | 0.126 | 0.07 | 0 | 0 | 0.0076 | 0.0073 | 0.005 | 0.0138 | 0
2019-07-18 05:00 | 78 | 0 | 0.045 | 0.0146 | 0.0004 | 0.064 | 0 | 0.25 | 0.0103 | 0.0021 | 0.07 | 0.057 | 0.01 | 0.074 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0.001 | 0 | 0.0671 | 0 | 0.07 | 0.0223 | 0.199 | 0.0048 | 0.0001 | 0.027 | 0 | 0.053 | 0.0184 | 0.076 | 0.043 | 0 | 0.126 | 0.07 | 0 | 0 | 0.0077 | 0.0084 | 0.005 | 0.0142 | 0
2019-07-18 06:00 | 79 | 0 | 0.0425 | 0.016 | 0.0004 | 0.051 | 0 | 0.25 | 0.0111 | 0.0023 | 0.07 | 0.05 | 0.011 | 0.081 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0.001 | 0 | 0.0631 | 0 | 0.07 | 0.0241 | 0.233 | 0.0051 | 0.0001 | 0.031 | 0 | 0.058 | 0.02 | 0.087 | 0.099 | 0 | 0.122 | 0.07 | 0 | 0 | 0.0093 | 0.0137 | 0.005 | 0.0164 | 0
2019-07-18 07:00 | 80 | 0 | 0.0425 | 0.0182 | 0.0005 | 0.055 | 0 | 0.25 | 0.0127 | 0.0027 | 0.11 | 0.052 | 0.003 | 0.093 | 0 | 0.001 | 0.25 | 0.001 | 0.009 | 0 | 0 | 0.1281 | 0 | 0.11 | 0.0275 | 0.249 | 0.0059 | 0.0001 | 0.035 | 0 | 0.0653 | 0.0228 | 0.061 | 0.102 | 0 | 0.016 | 0.11 | 0 | 0 | 0.0071 | 0.0262 | 0.005 | 0.0194 | 0
2019-07-18 08:00 | 81 | 0 | 0.0412 | 0.02 | 0.0005 | 0.05 | 0 | 0.3 | 0.0138 | 0.0029 | 0.11 | 0.051 | 0.001 | 0.108 | 0 | 0.001 | 0.3 | 0 | 0.019 | 0.013 | 0 | 0.1261 | 0 | 0.11 | 0.0301 | 0.258 | 0.0064 | 0.0001 | 0.032 | 0 | 0.0722 | 0.025 | 0.045 | 0.105 | 0 | 0 | 0.11 | 0 | 0 | 0.0058 | 0.0356 | 0.005 | 0.02 | 0
2019-07-18 09:00 | 82 | 0 | 0.0452 | 0.0201 | 0.0005 | 0.055 | 0 | 0.3 | 0.0139 | 0.0029 | 0.11 | 0.051 | 0 | 0.116 | 0 | 0.001 | 0.3 | 0.001 | 0.004 | 0.007 | 0 | 0.1441 | 0 | 0.11 | 0.0303 | 0.256 | 0.0065 | 0.0001 | 0.036 | 0 | 0.0719 | 0.0252 | 0 | 0.093 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0407 | 0.005 | 0.0191 | 0
2019-07-18 10:00 | 83 | 0 | 0.0458 | 0.019 | 0.0005 | 0.056 | 0 | 0.3 | 0.0132 | 0.0028 | 0.11 | 0.051 | 0 | 0.118 | 0 | 0.001 | 0.3 | 0.007 | 0 | 0.025 | 0 | 0.1751 | 0 | 0.11 | 0.0288 | 0.249 | 0.0062 | 0.0001 | 0.035 | 0 | 0.0683 | 0.024 | 0 | 0.117 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0414 | 0.005 | 0.0182 | 0
2019-07-18 11:00 | 84 | 0 | 0.0445 | 0.0187 | 0.0005 | 0.056 | 0 | 0.3 | 0.0124 | 0.0027 | 0.15 | 0.05 | 0 | 0.127 | 0 | 0.001 | 0.3 | 0.019 | 0 | 0.001 | 0 | 0.1311 | 0 | 0.15 | 0.0275 | 0.243 | 0.0058 | 0.0001 | 0.032 | 0 | 0.0654 | 0.023 | 0 | 0.121 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.0412 | 0.005 | 0.0188 | 0
2019-07-18 12:00 | 85 | 0 | 0.0443 | 0.0182 | 0.0004 | 0.057 | 0 | 0.4 | 0.0118 | 0.0026 | 0.15 | 0.05 | 0 | 0.116 | 0 | 0.001 | 0.4 | 0.001 | 0 | 0 | 0 | 0.1611 | 0 | 0.15 | 0.0265 | 0.232 | 0.0055 | 0.0001 | 0.034 | 0 | 0.0618 | 0.0223 | 0 | 0.105 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0401 | 0.005 | 0.0164 | 0
2019-07-18 13:00 | 86 | 0 | 0.0441 | 0.0182 | 0.0004 | 0.054 | 0 | 0.4 | 0.0111 | 0.0026 | 0.15 | 0.05 | 0 | 0.11 | 0 | 0.001 | 0.4 | 0.001 | 0.005 | 0.023 | 0 | 0.1591 | 0 | 0.15 | 0.0257 | 0.221 | 0.0052 | 0.0001 | 0.034 | 0 | 0.0598 | 0.0217 | 0 | 0.115 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.039 | 0.005 | 0.0173 | 0
2019-07-18 14:00 | 87 | 0 | 0.0421 | 0.0182 | 0.0004 | 0.055 | 0 | 0.5 | 0.011 | 0.0025 | 0.15 | 0.051 | 0 | 0.109 | 0 | 0.001 | 0.5 | 0.004 | 0 | 0 | 0 | 0.1611 | 0 | 0.15 | 0.0255 | 0.217 | 0.0052 | 0.0001 | 0.03 | 0 | 0.0584 | 0.0216 | 0 | 0.109 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.042 | 0.005 | 0.0183 | 0
2019-07-18 15:00 | 88 | 0 | 0.0442 | 0.0182 | 0.0004 | 0.052 | 0 | 0.55 | 0.0115 | 0.0026 | 0.15 | 0.051 | 0 | 0.108 | 0 | 0.001 | 0.55 | 0.003 | 0.003 | 0.015 | 0 | 0.1951 | 0 | 0.15 | 0.0261 | 0.211 | 0.0054 | 0.0001 | 0.03 | 0 | 0.0614 | 0.022 | 0 | 0.103 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0431 | 0.005 | 0.0174 | 0
2019-07-18 16:00 | 89 | 0 | 0.0427 | 0.0192 | 0.0005 | 0.056 | 0 | 0.629 | 0.0129 | 0.0028 | 0.23 | 0.051 | 0 | 0.12 | 0 | 0.001 | 0.593 | 0.007 | 0.013 | 0.039 | 0 | 0.1591 | 0 | 0.278 | 0.0284 | 0.209 | 0.006 | 0.0001 | 0.032 | 0 | 0.0668 | 0.0238 | 0.009 | 0.092 | 0 | 0 | 0.151 | 0 | 0 | 0.0035 | 0.0384 | 0.005 | 0.0172 | 0
2019-07-18 17:00 | 90 | 0 | 0.0451 | 0.0208 | 0.0007 | 0.051 | 0 | 0.629 | 0.0171 | 0.0031 | 0.23 | 0.024 | 0 | 0.122 | 0 | 0.001 | 0.593 | 0.001 | 0.016 | 0 | 0 | 0.1372 | 0 | 0.278 | 0.0346 | 0.215 | 0.0079 | 0.0001 | 0.031 | 0 | 0.0871 | 0.0284 | 0.054 | 0.086 | 0 | 0.023 | 0.143 | 0 | 0 | 0.0081 | 0.0212 | 0.005 | 0.0219 | 0
2019-07-18 18:00 | 91 | 0 | 0.0404 | 0.0208 | 0.0008 | 0.052 | 0 | 0.52 | 0.0185 | 0.0031 | 0.16 | 0.014 | 0 | 0.116 | 0 | 0.001 | 0.52 | 0.001 | 0.02 | 0.01 | 0 | 0.1732 | 0 | 0.16 | 0.0364 | 0.229 | 0.0085 | 0.0002 | 0.035 | 0 | 0.0921 | 0.0296 | 0.091 | 0.023 | 0 | 0.071 | 0.145 | 0 | 0 | 0.0091 | 0.0175 | 0.005 | 0.021 | 0
2019-07-18 19:00 | 92 | 0 | 0.0426 | 0.0212 | 0.0008 | 0.047 | 0 | 0.5 | 0.0189 | 0.0032 | 0.17 | 0.011 | 0.003 | 0.108 | 0 | 0.001 | 0.5 | 0.001 | 0.024 | 0.001 | 0 | 0.1602 | 0 | 0.17 | 0.0371 | 0.248 | 0.0087 | 0.0002 | 0.031 | 0 | 0.0949 | 0.0302 | 0.098 | 0.018 | 0 | 0.107 | 0.123 | 0 | 0 | 0.0083 | 0.0156 | 0.005 | 0.0204 | 0
2019-07-18 20:00 | 93 | 0 | 0.0374 | 0.0205 | 0.0008 | 0.048 | 0 | 0.3 | 0.0188 | 0.0031 | 0.11 | 0.022 | 0.003 | 0.097 | 0 | 0.001 | 0.3 | 0 | 0.018 | 0.014 | 0 | 0.1412 | 0 | 0.11 | 0.0365 | 0.236 | 0.0087 | 0.0002 | 0.027 | 0 | 0.0932 | 0.0296 | 0.086 | 0.014 | 0 | 0.113 | 0.11 | 0 | 0 | 0.008 | 0.0155 | 0.005 | 0.0198 | 0
2019-07-18 21:00 | 94 | 0 | 0.0372 | 0.02 | 0.0008 | 0.053 | 0 | 0.31 | 0.0185 | 0.003 | 0.09 | 0.053 | 0.005 | 0.098 | 0 | 0.001 | 0.31 | 0 | 0.012 | 0.001 | 0 | 0.1542 | 0 | 0.09 | 0.0358 | 0.236 | 0.0085 | 0.0002 | 0.028 | 0 | 0.0916 | 0.029 | 0.107 | 0.017 | 0 | 0.137 | 0.06 | 0 | 0 | 0.0088 | 0.0153 | 0.005 | 0.0183 | 0
2019-07-18 22:00 | 95 | 0 | 0.0392 | 0.0193 | 0.0008 | 0.065 | 0 | 0.2 | 0.0192 | 0.0029 | 0.09 | 0.054 | 0.007 | 0.098 | 0 | 0.001 | 0.2 | 0.001 | 0.011 | 0.001 | 0 | 0.0862 | 0 | 0.09 | 0.0362 | 0.248 | 0.0088 | 0.0002 | 0.031 | 0 | 0.095 | 0.0291 | 0.118 | 0.018 | 0 | 0.145 | 0.03 | 0 | 0 | 0.0095 | 0.0164 | 0.005 | 0.0197 | 0
2019-07-18 23:00 | 96 | 0 | 0.0374 | 0.0177 | 0.0007 | 0.067 | 0 | 0.1 | 0.0175 | 0.0028 | 0.05 | 0.054 | 0.006 | 0.101 | 0 | 0.001 | 0.1 | 0.017 | 0.008 | 0.001 | 0 | 0.0572 | 0 | 0.05 | 0.0331 | 0.23 | 0.008 | 0.0001 | 0.025 | 0 | 0.0868 | 0.0267 | 0.111 | 0.02 | 0 | 0.148 | 0.04 | 0 | 0 | 0.0099 | 0.0139 | 0.005 | 0.0183 | 0
2019-07-19 | 97 | 0 | 0.0333 | 0.0161 | 0.0006 | 0.069 | 0 | 0.1 | 0.0144 | 0.0026 | 0.04 | 0.054 | 0.006 | 0.084 | 0 | 0.001 | 0.1 | 0 | 0.008 | 0 | 0 | 0.0452 | 0 | 0.04 | 0.0283 | 0.232 | 0.0067 | 0.0001 | 0.026 | 0 | 0.0717 | 0.023 | 0.115 | 0.018 | 0 | 0.139 | 0.04 | 0 | 0 | 0.0083 | 0.0122 | 0.005 | 0.0157 | 0
2019-07-19 01:00 | 98 | 0 | 0.0366 | 0.0153 | 0.0005 | 0.062 | 0 | 0.1 | 0.0123 | 0.0024 | 0.04 | 0.054 | 0.006 | 0.089 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.002 | 0 | 0.0421 | 0 | 0.04 | 0.0251 | 0.219 | 0.0057 | 0.0001 | 0.028 | 0 | 0.0618 | 0.0206 | 0.108 | 0.022 | 0 | 0.146 | 0.04 | 0 | 0 | 0.008 | 0.0088 | 0.005 | 0.0149 | 0
2019-07-19 02:00 | 99 | 0 | 0.0351 | 0.0146 | 0.0004 | 0.067 | 0 | 0.1 | 0.0109 | 0.0023 | 0.04 | 0.055 | 0.006 | 0.079 | 0 | 0.001 | 0.1 | 0.001 | 0.008 | 0.006 | 0 | 0.0421 | 0 | 0.04 | 0.0229 | 0.213 | 0.005 | 0.0001 | 0.028 | 0 | 0.0563 | 0.0189 | 0.09 | 0.022 | 0 | 0.142 | 0.04 | 0 | 0 | 0.0077 | 0.0085 | 0.005 | 0.0152 | 0
2019-07-19 03:00 | 100 | 0 | 0.0319 | 0.0142 | 0.0004 | 0.062 | 0 | 0.1 | 0.0103 | 0.0023 | 0.07 | 0.055 | 0.006 | 0.092 | 0 | 0.001 | 0.1 | 0 | 0.008 | 0.002 | 0 | 0.0421 | 0 | 0.07 | 0.022 | 0.219 | 0.0048 | 0.0001 | 0.026 | 0 | 0.0525 | 0.0181 | 0.107 | 0.023 | 0 | 0.142 | 0.07 | 0 | 0 | 0.0076 | 0.0094 | 0.005 | 0.0139 | 0
2019-07-19 04:00 | 101 | 0 | 0.0348 | 0.0141 | 0.0004 | 0.064 | 0 | 0.25 | 0.01 | 0.0022 | 0.07 | 0.053 | 0.006 | 0.083 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0.001 | 0 | 0.0511 | 0 | 0.07 | 0.0216 | 0.203 | 0.0047 | 0.0001 | 0.027 | 0 | 0.0525 | 0.0178 | 0.098 | 0.027 | 0 | 0.139 | 0.07 | 0 | 0 | 0.0075 | 0.0083 | 0.005 | 0.0137 | 0
2019-07-19 05:00 | 102 | 0 | 0.0439 | 0.0141 | 0.0004 | 0.063 | 0 | 0.25 | 0.0101 | 0.0021 | 0.07 | 0.054 | 0.01 | 0.073 | 0 | 0.001 | 0.25 | 0.001 | 0.008 | 0 | 0 | 0.0701 | 0 | 0.07 | 0.0217 | 0.196 | 0.0047 | 0.0001 | 0.024 | 0 | 0.052 | 0.018 | 0.071 | 0.049 | 0 | 0.134 | 0.07 | 0 | 0 | 0.0075 | 0.0083 | 0.005 | 0.0168 | 0
2019-07-19 06:00 | 103 | 0 | 0.0413 | 0.0154 | 0.0004 | 0.043 | 0 | 0.25 | 0.0108 | 0.0024 | 0.07 | 0.053 | 0.01 | 0.095 | 0 | 0.001 | 0.25 | 0 | 0.008 | 0.001 | 0 | 0.0691 | 0 | 0.07 | 0.0234 | 0.227 | 0.005 | 0.0001 | 0.025 | 0 | 0.0565 | 0.0194 | 0.086 | 0.095 | 0 | 0.121 | 0.07 | 0 | 0 | 0.009 | 0.0176 | 0.005 | 0.0149 | 0
2019-07-19 07:00 | 104 | 0 | 0.0453 | 0.0179 | 0.0005 | 0.051 | 0 | 0.25 | 0.0125 | 0.0028 | 0.11 | 0.051 | 0.009 | 0.098 | 0 | 0.001 | 0.25 | 0.001 | 0.007 | 0 | 0 | 0.1201 | 0 | 0.11 | 0.0271 | 0.256 | 0.0058 | 0.0001 | 0.031 | 0 | 0.0645 | 0.0225 | 0.091 | 0.104 | 0 | 0.094 | 0.11 | 0 | 0 | 0.009 | 0.0272 | 0.005 | 0.0171 | 0
2019-07-19 08:00 | 105 | 0 | 0.0441 | 0.0197 | 0.0006 | 0.053 | 0 | 0.3 | 0.0141 | 0.003 | 0.11 | 0.051 | 0.001 | 0.106 | 0 | 0.001 | 0.3 | 0 | 0.019 | 0.018 | 0 | 0.1282 | 0 | 0.11 | 0.0302 | 0.264 | 0.0065 | 0.0001 | 0.031 | 0 | 0.0733 | 0.025 | 0.049 | 0.105 | 0 | 0 | 0.11 | 0 | 0 | 0.0047 | 0.0386 | 0.005 | 0.0198 | 0
2019-07-19 09:00 | 106 | 0 | 0.0431 | 0.0194 | 0.0006 | 0.055 | 0 | 0.3 | 0.0142 | 0.0031 | 0.11 | 0.051 | 0 | 0.112 | 0 | 0.001 | 0.3 | 0.011 | 0 | 0.002 | 0 | 0.1182 | 0 | 0.11 | 0.0302 | 0.261 | 0.0066 | 0.0001 | 0.034 | 0 | 0.0728 | 0.025 | 0.015 | 0.089 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0336 | 0.005 | 0.0185 | 0.013
2019-07-19 10:00 | 107 | 0 | 0.0437 | 0.0186 | 0.0005 | 0.054 | 0 | 0.3 | 0.0132 | 0.0029 | 0.11 | 0.052 | 0 | 0.116 | 0 | 0.001 | 0.3 | 0.003 | 0 | 0 | 0 | 0.1681 | 0 | 0.11 | 0.0284 | 0.261 | 0.0061 | 0.0001 | 0.031 | 0 | 0.0678 | 0.0237 | 0 | 0.102 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0364 | 0.005 | 0.0188 | 0.008
2019-07-19 11:00 | 108 | 0 | 0.0454 | 0.0183 | 0.0005 | 0.045 | 0 | 0.3 | 0.0123 | 0.0029 | 0.15 | 0.051 | 0 | 0.128 | 0 | 0.001 | 0.3 | 0.001 | 0 | 0 | 0 | 0.1271 | 0 | 0.15 | 0.0271 | 0.247 | 0.0057 | 0.0001 | 0.032 | 0 | 0.0648 | 0.0227 | 0 | 0.106 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.0362 | 0.005 | 0.0185 | 0
2019-07-19 12:00 | 109 | 0 | 0.043 | 0.0174 | 0.0004 | 0.054 | 0 | 0.4 | 0.0114 | 0.0028 | 0.15 | 0.05 | 0 | 0.116 | 0 | 0.001 | 0.4 | 0.005 | 0 | 0.028 | 0 | 0.1371 | 0 | 0.15 | 0.0255 | 0.232 | 0.0053 | 0.0001 | 0.031 | 0 | 0.0597 | 0.0215 | 0 | 0.088 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0369 | 0.005 | 0.0157 | 0
2019-07-19 13:00 | 110 | 0 | 0.0438 | 0.0173 | 0.0004 | 0.055 | 0 | 0.4 | 0.011 | 0.0027 | 0.15 | 0.051 | 0 | 0.109 | 0 | 0.001 | 0.4 | 0.001 | 0.003 | 0 | 0 | 0.1611 | 0 | 0.15 | 0.0249 | 0.233 | 0.0051 | 0.0001 | 0.033 | 0 | 0.0587 | 0.021 | 0 | 0.073 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0329 | 0.005 | 0.0165 | 0
2019-07-19 14:00 | 111 | 0 | 0.0449 | 0.0174 | 0.0004 | 0.053 | 0 | 0.5 | 0.0111 | 0.0028 | 0.15 | 0.05 | 0 | 0.113 | 0 | 0.001 | 0.5 | 0.001 | 0.005 | 0.032 | 0 | 0.1561 | 0 | 0.15 | 0.0251 | 0.229 | 0.0052 | 0.0001 | 0.029 | 0 | 0.0582 | 0.0212 | 0 | 0.07 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0379 | 0.005 | 0.0157 | 0
2019-07-19 15:00 | 112 | 0 | 0.0439 | 0.0172 | 0.0004 | 0.055 | 0 | 0.55 | 0.0111 | 0.0028 | 0.15 | 0.05 | 0 | 0.128 | 0 | 0.001 | 0.55 | 0.018 | 0.004 | 0 | 0 | 0.1431 | 0 | 0.15 | 0.025 | 0.225 | 0.0052 | 0.0001 | 0.031 | 0 | 0.0591 | 0.021 | 0 | 0.061 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0369 | 0.005 | 0.0165 | 0
2019-07-19 16:00 | 113 | 0 | 0.0444 | 0.0181 | 0.0005 | 0.056 | 0 | 0.629 | 0.0125 | 0.003 | 0.23 | 0.047 | 0 | 0.147 | 0 | 0.001 | 0.593 | 0.001 | 0.006 | 0.012 | 0 | 0.1461 | 0 | 0.278 | 0.0273 | 0.215 | 0.0058 | 0.0001 | 0.033 | 0 | 0.0647 | 0.0228 | 0 | 0.049 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0362 | 0.005 | 0.0203 | 0
2019-07-19 17:00 | 114 | 0 | 0.0446 | 0.0198 | 0.0007 | 0.06 | 0 | 0.629 | 0.0163 | 0.0032 | 0.23 | 0.013 | 0 | 0.139 | 0 | 0.001 | 0.593 | 0 | 0.017 | 0 | 0 | 0.2132 | 0 | 0.278 | 0.0329 | 0.225 | 0.0075 | 0.0001 | 0.031 | 0 | 0.0828 | 0.0271 | 0.003 | 0.047 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.017 | 0.005 | 0.019 | 0
2019-07-19 18:00 | 115 | 0 | 0.0423 | 0.0205 | 0.0008 | 0.051 | 0 | 0.52 | 0.0182 | 0.0032 | 0.16 | 0.011 | 0 | 0.121 | 0 | 0.001 | 0.52 | 0 | 0.027 | 0.015 | 0 | 0.1702 | 0 | 0.16 | 0.0358 | 0.231 | 0.0084 | 0.0001 | 0.032 | 0 | 0.0907 | 0.0292 | 0.053 | 0.025 | 0 | 0.051 | 0.145 | 0 | 0 | 0.004 | 0.0144 | 0.005 | 0.0197 | 0
2019-07-19 19:00 | 116 | 0 | 0.0392 | 0.0204 | 0.0007 | 0.049 | 0 | 0.5 | 0.0179 | 0.0032 | 0.17 | 0.009 | 0.001 | 0.12 | 0 | 0.001 | 0.5 | 0.049 | 0.024 | 0 | 0 | 0.1512 | 0 | 0.17 | 0.0354 | 0.228 | 0.0083 | 0.0001 | 0.03 | 0 | 0.0903 | 0.0288 | 0.094 | 0.023 | 0 | 0.104 | 0.123 | 0 | 0 | 0.007 | 0.0123 | 0.005 | 0.0196 | 0
2019-07-19 20:00 | 117 | 0 | 0.04 | 0.0198 | 0.0007 | 0.057 | 0 | 0.3 | 0.0177 | 0.0032 | 0.11 | 0.011 | 0.001 | 0.113 | 0 | 0.001 | 0.3 | 0.009 | 0.029 | 0.02 | 0 | 0.1572 | 0 | 0.11 | 0.0347 | 0.22 | 0.0081 | 0.0001 | 0.031 | 0 | 0.0878 | 0.0282 | 0.101 | 0.022 | 0 | 0.117 | 0.11 | 0 | 0 | 0.0077 | 0.0092 | 0.005 | 0.0191 | 0
2019-07-19 21:00 | 118 | 0 | 0.0387 | 0.0191 | 0.0007 | 0.055 | 0 | 0.31 | 0.0173 | 0.0031 | 0.09 | 0.054 | 0.004 | 0.102 | 0 | 0.001 | 0.31 | 0.001 | 0.016 | 0.001 | 0 | 0.1422 | 0 | 0.09 | 0.0337 | 0.22 | 0.008 | 0.0001 | 0.029 | 0 | 0.0857 | 0.0274 | 0.104 | 0.021 | 0 | 0.14 | 0.06 | 0 | 0 | 0.0085 | 0.008 | 0.005 | 0.0184 | 0.057
2019-07-19 22:00 | 119 | 0 | 0.037 | 0.019 | 0.0008 | 0.067 | 0 | 0.2 | 0.0187 | 0.003 | 0.09 | 0.053 | 0.005 | 0.105 | 0 | 0.001 | 0.2 | 0.001 | 0.012 | 0.001 | 0 | 0.0872 | 0 | 0.09 | 0.0354 | 0.223 | 0.0086 | 0.0002 | 0.03 | 0 | 0.0929 | 0.0286 | 0.114 | 0.02 | 0 | 0.149 | 0.03 | 0 | 0 | 0.0094 | 0.0103 | 0.005 | 0.0185 | 0.058
2019-07-19 23:00 | 120 | 0 | 0.0374 | 0.0178 | 0.0007 | 0.061 | 0 | 0.1 | 0.0174 | 0.0028 | 0.05 | 0.054 | 0.004 | 0.079 | 0 | 0.001 | 0.1 | 0 | 0.01 | 0.001 | 0 | 0.0492 | 0 | 0.05 | 0.0329 | 0.226 | 0.008 | 0.0001 | 0.03 | 0 | 0.0863 | 0.0266 | 0.12 | 0.022 | 0 | 0.15 | 0.04 | 0 | 0 | 0.0099 | 0.0099 | 0.005 | 0.0183 | 0
2019-07-20 | 121 | 0 | 0.0333 | 0.0159 | 0.0006 | 0.064 | 0 | 0.1 | 0.0146 | 0.0026 | 0.04 | 0.053 | 0.005 | 0.05 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0 | 0 | 0.0432 | 0 | 0.04 | 0.0284 | 0.23 | 0.0067 | 0.0001 | 0.027 | 0 | 0.0724 | 0.023 | 0.105 | 0.02 | 0 | 0.143 | 0.04 | 0 | 0 | 0.0082 | 0.0082 | 0.005 | 0.0156 | 0
2019-07-20 01:00 | 122 | 0 | 0.0345 | 0.0148 | 0.0005 | 0.062 | 0 | 0.1 | 0.0122 | 0.0024 | 0.04 | 0.055 | 0.004 | 0.047 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0441 | 0 | 0.04 | 0.0247 | 0.224 | 0.0056 | 0.0001 | 0.027 | 0 | 0.0613 | 0.0202 | 0.1 | 0.022 | 0 | 0.141 | 0.04 | 0 | 0 | 0.0078 | 0.0087 | 0.005 | 0.0144 | 0
2019-07-20 02:00 | 123 | 0 | 0.0341 | 0.0143 | 0.0004 | 0.063 | 0 | 0.1 | 0.0109 | 0.0024 | 0.04 | 0.054 | 0.005 | 0.056 | 0 | 0.001 | 0.1 | 0.001 | 0.009 | 0.001 | 0 | 0.0421 | 0 | 0.04 | 0.0228 | 0.218 | 0.005 | 0.0001 | 0.028 | 0 | 0.0563 | 0.0187 | 0.095 | 0.024 | 0 | 0.137 | 0.04 | 0 | 0 | 0.0076 | 0.0085 | 0.005 | 0.0149 | 0
2019-07-20 03:00 | 124 | 0 | 0.0358 | 0.014 | 0.0004 | 0.056 | 0 | 0.1 | 0.0103 | 0.0024 | 0.07 | 0.053 | 0.004 | 0.051 | 0 | 0.001 | 0.1 | 0.001 | 0.01 | 0.001 | 0 | 0.0411 | 0 | 0.07 | 0.0218 | 0.208 | 0.0048 | 0.0001 | 0.028 | 0 | 0.0524 | 0.018 | 0.091 | 0.023 | 0 | 0.135 | 0.07 | 0 | 0 | 0.0075 | 0.0083 | 0.005 | 0.0147 | 0
2019-07-20 04:00 | 125 | 0 | 0.0368 | 0.014 | 0.0004 | 0.061 | 0 | 0.25 | 0.01 | 0.0022 | 0.07 | 0.052 | 0.004 | 0.038 | 0 | 0.001 | 0.25 | 0 | 0.009 | 0.001 | 0 | 0.0401 | 0 | 0.07 | 0.0216 | 0.205 | 0.0047 | 0.0001 | 0.027 | 0 | 0.0525 | 0.0178 | 0.109 | 0.025 | 0 | 0.133 | 0.07 | 0 | 0 | 0.0075 | 0.0073 | 0.005 | 0.0137 | 0
2019-07-20 05:00 | 126 | 0 | 0.036 | 0.0146 | 0.0004 | 0.056 | 0 | 0.25 | 0.0102 | 0.0023 | 0.07 | 0.054 | 0.005 | 0.033 | 0 | 0.001 | 0.25 | 0.019 | 0.009 | 0 | 0 | 0.0471 | 0 | 0.07 | 0.022 | 0.207 | 0.0047 | 0.0001 | 0.032 | 0 | 0.0523 | 0.0183 | 0.073 | 0.045 | 0 | 0.124 | 0.07 | 0 | 0 | 0.0077 | 0.0084 | 0.005 | 0.0141 | 0
2019-07-20 06:00 | 127 | 0 | 0.0352 | 0.0153 | 0.0004 | 0.054 | 0 | 0.25 | 0.0102 | 0.0025 | 0.07 | 0.051 | 0.002 | 0.033 | 0 | 0.001 | 0.25 | 0.001 | 0.007 | 0 | 0 | 0.0671 | 0 | 0.07 | 0.0225 | 0.213 | 0.0047 | 0.0001 | 0.023 | 0 | 0.0537 | 0.0187 | 0.071 | 0.047 | 0 | 0.09 | 0.07 | 0 | 0 | 0.007 | 0.0065 | 0.005 | 0.0147 | 0
2019-07-20 07:00 | 128 | 0 | 0.0438 | 0.0167 | 0.0004 | 0.051 | 0 | 0.25 | 0.0113 | 0.0029 | 0.11 | 0.051 | 0 | 0.052 | 0 | 0.001 | 0.25 | 0.001 | 0.006 | 0.001 | 0 | 0.1081 | 0 | 0.11 | 0.0248 | 0.22 | 0.0053 | 0.0001 | 0.027 | 0 | 0.0584 | 0.0207 | 0.075 | 0.057 | 0 | 0.027 | 0.11 | 0 | 0 | 0.0035 | 0.0208 | 0.005 | 0.015 | 0
2019-07-20 08:00 | 129 | 0 | 0.0424 | 0.0174 | 0.0005 | 0.05 | 0 | 0.3 | 0.0133 | 0.0032 | 0.11 | 0.051 | 0.002 | 0.075 | 0 | 0.001 | 0.3 | 0 | 0.011 | 0 | 0 | 0.1221 | 0 | 0.11 | 0.0277 | 0.225 | 0.0062 | 0.0001 | 0.031 | 0 | 0.0685 | 0.0229 | 0.088 | 0.059 | 0 | 0.07 | 0.11 | 0 | 0 | 0.0098 | 0.0362 | 0.005 | 0.0167 | 0
2019-07-20 09:00 | 130 | 0 | 0.0478 | 0.0178 | 0.0006 | 0.051 | 0 | 0.3 | 0.0148 | 0.0032 | 0.11 | 0.051 | 0.001 | 0.073 | 0 | 0.001 | 0.3 | 0.001 | 0.027 | 0 | 0 | 0.1202 | 0 | 0.11 | 0.0298 | 0.247 | 0.0068 | 0.0001 | 0.035 | 0 | 0.0743 | 0.0245 | 0.078 | 0.049 | 0 | 0.06 | 0.11 | 0 | 0 | 0.0089 | 0.0395 | 0.005 | 0.0171 | 0
2019-07-20 10:00 | 131 | 0 | 0.0446 | 0.0172 | 0.0006 | 0.048 | 0 | 0.3 | 0.0146 | 0.0031 | 0.11 | 0.014 | 0 | 0.069 | 0 | 0.001 | 0.3 | 0 | 0.018 | 0.001 | 0 | 0.1462 | 0 | 0.11 | 0.0292 | 0.248 | 0.0067 | 0.0001 | 0.033 | 0 | 0.0731 | 0.024 | 0.083 | 0.061 | 0 | 0.053 | 0.11 | 0 | 0 | 0.0097 | 0.0404 | 0.005 | 0.0167 | 0
2019-07-20 11:00 | 132 | 0 | 0.0495 | 0.0171 | 0.0006 | 0.049 | 0 | 0.3 | 0.0141 | 0.0031 | 0.15 | 0.005 | 0.004 | 0.073 | 0 | 0.001 | 0.3 | 0.001 | 0.022 | 0 | 0 | 0.1312 | 0 | 0.15 | 0.0285 | 0.254 | 0.0065 | 0.0001 | 0.026 | 0 | 0.072 | 0.0235 | 0.066 | 0.055 | 0 | 0.095 | 0.13 | 0 | 0 | 0.0097 | 0.0443 | 0.005 | 0.0165 | 0
2019-07-20 12:00 | 133 | 0 | 0.0452 | 0.0164 | 0.0006 | 0.05 | 0 | 0.4 | 0.0138 | 0.003 | 0.15 | 0.005 | 0 | 0.064 | 0 | 0.001 | 0.4 | 0.001 | 0.016 | 0.034 | 0 | 0.1442 | 0 | 0.15 | 0.0277 | 0.245 | 0.0064 | 0.0001 | 0.026 | 0 | 0.0694 | 0.0229 | 0.017 | 0.044 | 0 | 0 | 0.122 | 0 | 0 | 0.0014 | 0.0232 | 0.005 | 0.0159 | 0
2019-07-20 13:00 | 134 | 0 | 0.0441 | 0.0166 | 0.0005 | 0.056 | 0 | 0.4 | 0.013 | 0.003 | 0.15 | 0.006 | 0 | 0.08 | 0 | 0.001 | 0.4 | 0.004 | 0.004 | 0.07 | 0 | 0.1381 | 0 | 0.15 | 0.0268 | 0.235 | 0.006 | 0.0001 | 0.025 | 0 | 0.0668 | 0.0222 | 0 | 0.038 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0121 | 0.005 | 0.017 | 0
2019-07-20 14:00 | 135 | 0 | 0.044 | 0.0165 | 0.0005 | 0.052 | 0 | 0.5 | 0.0124 | 0.0029 | 0.15 | 0.005 | 0 | 0.093 | 0 | 0.001 | 0.5 | 0 | 0 | 0.04 | 0 | 0.1701 | 0 | 0.15 | 0.0261 | 0.227 | 0.0058 | 0.0001 | 0.022 | 0 | 0.0635 | 0.0218 | 0 | 0.037 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.013 | 0.005 | 0.015 | 0
2019-07-20 15:00 | 136 | 0 | 0.0429 | 0.0163 | 0.0005 | 0.049 | 0 | 0.55 | 0.0122 | 0.003 | 0.15 | 0.006 | 0 | 0.1 | 0 | 0.001 | 0.55 | 0.001 | 0.015 | 0 | 0 | 0.1591 | 0 | 0.15 | 0.0257 | 0.22 | 0.0057 | 0.0001 | 0.025 | 0 | 0.0633 | 0.0214 | 0 | 0.037 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0119 | 0.005 | 0.0158 | 0
2019-07-20 16:00 | 137 | 0 | 0.0412 | 0.0169 | 0.0005 | 0.055 | 0 | 0.629 | 0.0128 | 0.0031 | 0.23 | 0.006 | 0 | 0.092 | 0 | 0.001 | 0.593 | 0.001 | 0.005 | 0.022 | 0 | 0.1701 | 0 | 0.278 | 0.0268 | 0.22 | 0.0059 | 0.0001 | 0.022 | 0 | 0.0652 | 0.0223 | 0 | 0.024 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0131 | 0.005 | 0.0183 | 0
2019-07-20 17:00 | 138 | 0 | 0.0411 | 0.0178 | 0.0007 | 0.057 | 0 | 0.629 | 0.016 | 0.0033 | 0.23 | 0.005 | 0 | 0.076 | 0 | 0.001 | 0.593 | 0.001 | 0.012 | 0.004 | 0 | 0.1512 | 0 | 0.278 | 0.0313 | 0.222 | 0.0074 | 0.0001 | 0.024 | 0 | 0.0806 | 0.0256 | 0 | 0.02 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0127 | 0.005 | 0.0173 | 0
2019-07-20 18:00 | 139 | 0 | 0.0389 | 0.0192 | 0.0008 | 0.049 | 0 | 0.52 | 0.018 | 0.0034 | 0.16 | 0.007 | 0 | 0.073 | 0 | 0.001 | 0.52 | 0 | 0.015 | 0.016 | 0 | 0.1582 | 0 | 0.16 | 0.0346 | 0.228 | 0.0083 | 0.0001 | 0.024 | 0 | 0.0888 | 0.0281 | 0 | 0.012 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0092 | 0.005 | 0.0176 | 0
2019-07-20 19:00 | 140 | 0 | 0.0391 | 0.0197 | 0.0008 | 0.051 | 0 | 0.5 | 0.0184 | 0.0034 | 0.17 | 0.005 | 0 | 0.064 | 0 | 0.001 | 0.5 | 0.001 | 0.016 | 0 | 0 | 0.1312 | 0 | 0.17 | 0.0354 | 0.232 | 0.0085 | 0.0002 | 0.021 | 0 | 0.0919 | 0.0287 | 0 | 0.015 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0083 | 0.005 | 0.019 | 0
2019-07-20 20:00 | 141 | 0 | 0.0389 | 0.0189 | 0.0008 | 0.054 | 0 | 0.3 | 0.0184 | 0.0033 | 0.11 | 0.006 | 0 | 0.049 | 0 | 0.001 | 0.3 | 0.001 | 0.015 | 0.001 | 0 | 0.1242 | 0 | 0.11 | 0.035 | 0.223 | 0.0085 | 0.0002 | 0.018 | 0 | 0.0906 | 0.0283 | 0.04 | 0.021 | 0 | 0.063 | 0.11 | 0 | 0 | 0.0044 | 0.0092 | 0.005 | 0.0184 | 0
2019-07-20 21:00 | 142 | 0 | 0.0378 | 0.0188 | 0.0008 | 0.057 | 0 | 0.31 | 0.0182 | 0.0032 | 0.09 | 0.006 | 0.004 | 0.045 | 0 | 0.001 | 0.31 | 0.001 | 0.011 | 0 | 0 | 0.1402 | 0 | 0.09 | 0.0346 | 0.231 | 0.0084 | 0.0002 | 0.018 | 0 | 0.0894 | 0.0279 | 0.059 | 0.019 | 0 | 0.123 | 0.06 | 0 | 0 | 0.0073 | 0.0081 | 0.005 | 0.0182 | 0
2019-07-20 22:00 | 143 | 0 | 0.038 | 0.0189 | 0.0008 | 0.06 | 0 | 0.2 | 0.019 | 0.0031 | 0.09 | 0.008 | 0.005 | 0.045 | 0 | 0.001 | 0.2 | 0 | 0.009 | 0.001 | 0 | 0.0852 | 0 | 0.09 | 0.0356 | 0.229 | 0.0087 | 0.0002 | 0.02 | 0 | 0.0938 | 0.0287 | 0.075 | 0.02 | 0 | 0.133 | 0.03 | 0 | 0 | 0.0094 | 0.0103 | 0.005 | 0.0184 | 0
2019-07-20 23:00 | 144 | 0 | 0.0362 | 0.0174 | 0.0007 | 0.064 | 0 | 0.1 | 0.0171 | 0.0028 | 0.05 | 0.008 | 0.004 | 0.038 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0572 | 0 | 0.05 | 0.0324 | 0.231 | 0.0079 | 0.0001 | 0.021 | 0 | 0.0849 | 0.0261 | 0.061 | 0.02 | 0 | 0.129 | 0.04 | 0 | 0 | 0.0088 | 0.0098 | 0.005 | 0.018 | 0
2019-07-21 | 145 | 0 | 0.0342 | 0.0157 | 0.0006 | 0.062 | 0 | 0.1 | 0.0144 | 0.0026 | 0.04 | 0.007 | 0.005 | 0.033 | 0 | 0.001 | 0.1 | 0.013 | 0.008 | 0.001 | 0 | 0.0572 | 0 | 0.04 | 0.0279 | 0.233 | 0.0066 | 0.0001 | 0.019 | 0 | 0.0711 | 0.0226 | 0.042 | 0.02 | 0 | 0.12 | 0.04 | 0 | 0 | 0.0071 | 0.0082 | 0.005 | 0.0143 | 0
2019-07-21 01:00 | 146 | 0 | 0.0344 | 0.0146 | 0.0005 | 0.055 | 0 | 0.1 | 0.0122 | 0.0024 | 0.04 | 0.007 | 0.004 | 0.034 | 0 | 0.001 | 0.1 | 0.01 | 0.008 | 0.001 | 0 | 0.0441 | 0 | 0.04 | 0.0245 | 0.231 | 0.0056 | 0.0001 | 0.021 | 0 | 0.061 | 0.02 | 0.044 | 0.019 | 0 | 0.06 | 0.04 | 0 | 0 | 0.0077 | 0.0087 | 0.005 | 0.0142 | 0
2019-07-21 02:00 | 147 | 0 | 0.032 | 0.014 | 0.0004 | 0.063 | 0 | 0.1 | 0.011 | 0.0023 | 0.04 | 0.008 | 0.005 | 0.03 | 0 | 0.001 | 0.1 | 0.001 | 0.008 | 0 | 0 | 0.0421 | 0 | 0.04 | 0.0226 | 0.22 | 0.0051 | 0.0001 | 0.021 | 0 | 0.0564 | 0.0186 | 0.04 | 0.02 | 0 | 0.036 | 0.04 | 0 | 0 | 0.0075 | 0.0084 | 0.005 | 0.0137 | 0
2019-07-21 03:00 | 148 | 0 | 0.0338 | 0.0137 | 0.0004 | 0.066 | 0 | 0.1 | 0.0102 | 0.0023 | 0.07 | 0.007 | 0.004 | 0.032 | 0 | 0.001 | 0.1 | 0 | 0.009 | 0.001 | 0 | 0.0391 | 0 | 0.07 | 0.0216 | 0.213 | 0.0047 | 0.0001 | 0.019 | 0 | 0.0521 | 0.0178 | 0.041 | 0.018 | 0 | 0.037 | 0.07 | 0 | 0 | 0.0074 | 0.0083 | 0.005 | 0.0144 | 0
2019-07-21 04:00 | 149 | 0 | 0.0316 | 0.0134 | 0.0004 | 0.063 | 0 | 0.25 | 0.0099 | 0.0022 | 0.07 | 0.008 | 0.005 | 0.032 | 0 | 0.001 | 0.25 | 0.001 | 0.009 | 0.001 | 0 | 0.0411 | 0 | 0.07 | 0.021 | 0.212 | 0.0046 | 0.0001 | 0.021 | 0 | 0.0515 | 0.0173 | 0.045 | 0.021 | 0 | 0.037 | 0.07 | 0 | 0 | 0.0072 | 0.0082 | 0.005 | 0.0131 | 0
2019-07-21 05:00 | 150 | 0 | 0.0317 | 0.0138 | 0.0004 | 0.061 | 0 | 0.25 | 0.0098 | 0.0023 | 0.07 | 0.006 | 0.005 | 0.03 | 0 | 0.001 | 0.25 | 0 | 0.007 | 0.001 | 0 | 0.0551 | 0 | 0.07 | 0.0211 | 0.214 | 0.0046 | 0.0001 | 0.019 | 0 | 0.0503 | 0.0174 | 0.037 | 0.019 | 0 | 0.033 | 0.07 | 0 | 0 | 0.0074 | 0.0072 | 0.005 | 0.0124 | 0
2019-07-21 06:00 | 151 | 0 | 0.0349 | 0.0146 | 0.0004 | 0.054 | 0 | 0.25 | 0.0098 | 0.0026 | 0.07 | 0.005 | 0.002 | 0.028 | 0 | 0.001 | 0.25 | 0.002 | 0.008 | 0 | 0 | 0.0591 | 0 | 0.07 | 0.0216 | 0.22 | 0.0045 | 0.0001 | 0.017 | 0 | 0.0516 | 0.0179 | 0.029 | 0.027 | 0 | 0.012 | 0.07 | 0 | 0 | 0.0057 | 0.0063 | 0.005 | 0.0141 | 0
2019-07-21 07:00 | 152 | 0 | 0.0412 | 0.0153 | 0.0004 | 0.044 | 0 | 0.25 | 0.0104 | 0.0029 | 0.11 | 0.005 | 0 | 0.029 | 0 | 0.001 | 0.25 | 0 | 0.006 | 0 | 0 | 0.1201 | 0 | 0.11 | 0.0229 | 0.231 | 0.0049 | 0.0001 | 0.019 | 0 | 0.0539 | 0.019 | 0.008 | 0.022 | 0 | 0 | 0.11 | 0 | 0 | 0.003 | 0.0095 | 0.005 | 0.0148 | 0
2019-07-21 08:00 | 153 | 0 | 0.0445 | 0.0153 | 0.0005 | 0.053 | 0 | 0.3 | 0.0119 | 0.0032 | 0.11 | 0.005 | 0 | 0.032 | 0 | 0.001 | 0.3 | 0 | 0.002 | 0.001 | 0 | 0.1271 | 0 | 0.11 | 0.0246 | 0.226 | 0.0055 | 0.0001 | 0.024 | 0 | 0.0612 | 0.0203 | 0 | 0.023 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0117 | 0.005 | 0.0139 | 0
2019-07-21 09:00 | 154 | 0 | 0.0428 | 0.0151 | 0.0005 | 0.048 | 0 | 0.3 | 0.0132 | 0.0031 | 0.11 | 0.007 | 0 | 0.032 | 0 | 0.001 | 0.3 | 0.001 | 0.004 | 0.009 | 0 | 0.1212 | 0 | 0.11 | 0.0261 | 0.246 | 0.0061 | 0.0001 | 0.027 | 0 | 0.0659 | 0.0214 | 0 | 0.025 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0119 | 0.005 | 0.0147 | 0
2019-07-21 10:00 | 155 | 0 | 0.0437 | 0.0145 | 0.0006 | 0.048 | 0 | 0.3 | 0.0136 | 0.0029 | 0.11 | 0.005 | 0 | 0.03 | 0 | 0.001 | 0.3 | 0.001 | 0 | 0 | 0 | 0.1232 | 0 | 0.11 | 0.0261 | 0.24 | 0.0063 | 0.0001 | 0.026 | 0 | 0.0672 | 0.0213 | 0 | 0.028 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0.0119 | 0.005 | 0.0143 | 0
2019-07-21 11:00 | 156 | 0 | 0.0427 | 0.0144 | 0.0006 | 0.05 | 0 | 0.3 | 0.0135 | 0.0029 | 0.15 | 0.006 | 0 | 0.028 | 0 | 0.001 | 0.3 | 0.04 | 0 | 0 | 0 | 0.1572 | 0 | 0.15 | 0.026 | 0.241 | 0.0062 | 0.0001 | 0.023 | 0 | 0.0679 | 0.0212 | 0 | 0.031 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.0119 | 0.005 | 0.0132 | 0
2019-07-21 12:00 | 157 | 0 | 0.0415 | 0.0139 | 0.0006 | 0.051 | 0 | 0.4 | 0.0132 | 0.0028 | 0.15 | 0.007 | 0 | 0.03 | 0 | 0.001 | 0.4 | 0.001 | 0 | 0.029 | 0 | 0.1742 | 0 | 0.15 | 0.0253 | 0.245 | 0.0061 | 0.0001 | 0.026 | 0 | 0.0654 | 0.0207 | 0 | 0.034 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0.0128 | 0.005 | 0.0137 | 0
2019-07-21 13:00 | 158 | 0 | 0.0422 | 0.0136 | 0.0005 | 0.053 | 0 | 0.4 | 0.0124 | 0.0027 | 0.15 | 0.005 | 0 | 0.031 | 0 | 0.001 | 0.4 | 0.001 | 0 | 0.044 | 0 | 0.1291 | 0 | 0.15 | 0.0241 | 0.234 | 0.0057 | 0.0001 | 0.024 | 0 | 0.0625 | 0.0198 | 0 | 0.032 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0116 | 0.005 | 0.0135 | 0
2019-07-21 14:00 | 159 | 0 | 0.0421 | 0.0133 | 0.0005 | 0.051 | 0 | 0.5 | 0.0121 | 0.0027 | 0.15 | 0.006 | 0 | 0.03 | 0 | 0.001 | 0.5 | 0.001 | 0 | 0.04 | 0 | 0.1501 | 0 | 0.15 | 0.0235 | 0.219 | 0.0056 | 0.0001 | 0.023 | 0 | 0.0602 | 0.0193 | 0 | 0.032 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0115 | 0.005 | 0.0131 | 0
2019-07-21 15:00 | 160 | 0 | 0.042 | 0.0133 | 0.0005 | 0.055 | 0 | 0.55 | 0.0115 | 0.0027 | 0.15 | 0.006 | 0 | 0.031 | 0 | 0.001 | 0.55 | 0.003 | 0 | 0.054 | 0 | 0.1411 | 0 | 0.15 | 0.0229 | 0.213 | 0.0053 | 0.0001 | 0.023 | 0 | 0.0588 | 0.0189 | 0 | 0.031 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0114 | 0.005 | 0.0121 | 0
2019-07-21 16:00 | 161 | 0 | 0.0394 | 0.0142 | 0.0005 | 0.05 | 0 | 0.629 | 0.0125 | 0.0028 | 0.23 | 0.006 | 0 | 0.032 | 0 | 0.001 | 0.593 | 0.003 | 0.005 | 0.011 | 0 | 0.1661 | 0 | 0.278 | 0.0246 | 0.205 | 0.0058 | 0.0001 | 0.023 | 0 | 0.0623 | 0.0202 | 0 | 0.03 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0.0117 | 0.005 | 0.014 | 0
2019-07-21 17:00 | 162 | 0 | 0.0409 | 0.0169 | 0.0007 | 0.049 | 0 | 0.629 | 0.0161 | 0.003 | 0.23 | 0.006 | 0 | 0.029 | 0 | 0.001 | 0.593 | 0 | 0.003 | 0.001 | 0 | 0.1542 | 0 | 0.278 | 0.0308 | 0.204 | 0.0074 | 0.0001 | 0.024 | 0 | 0.0803 | 0.025 | 0 | 0.033 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.0126 | 0.005 | 0.0165 | 0
2019-07-21 18:00 | 163 | 0 | 0.0378 | 0.0187 | 0.0008 | 0.049 | 0 | 0.52 | 0.0184 | 0.0032 | 0.16 | 0.006 | 0 | 0.029 | 0 | 0.001 | 0.52 | 0.001 | 0.016 | 0 | 0 | 0.1552 | 0 | 0.16 | 0.0348 | 0.215 | 0.0085 | 0.0002 | 0.022 | 0 | 0.0905 | 0.0282 | 0 | 0.037 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0.0082 | 0.005 | 0.0172 | 0
2019-07-21 19:00 | 164 | 0 | 0.0358 | 0.0187 | 0.0008 | 0.05 | 0 | 0.5 | 0.0181 | 0.0032 | 0.17 | 0.006 | 0 | 0.03 | 0 | 0.001 | 0.5 | 0.001 | 0.02 | 0 | 0 | 0.1352 | 0 | 0.17 | 0.0344 | 0.231 | 0.0083 | 0.0001 | 0.019 | 0 | 0.0898 | 0.0278 | 0.041 | 0.035 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0.0091 | 0.005 | 0.0181 | 0
2019-07-21 20:00 | 165 | 0 | 0.0347 | 0.0182 | 0.0008 | 0.05 | 0 | 0.3 | 0.0185 | 0.003 | 0.11 | 0.005 | 0 | 0.031 | 0 | 0.001 | 0.3 | 0.001 | 0.019 | 0 | 0 | 0.1232 | 0 | 0.11 | 0.0346 | 0.227 | 0.0085 | 0.0002 | 0.019 | 0 | 0.0903 | 0.0278 | 0.074 | 0.029 | 0 | 0.068 | 0.11 | 0 | 0 | 0.0051 | 0.0081 | 0.005 | 0.0167 | 0.004
2019-07-21 21:00 | 166 | 0 | 0.0377 | 0.0182 | 0.0008 | 0.049 | 0 | 0.31 | 0.0185 | 0.0029 | 0.09 | 0.007 | 0.004 | 0.041 | 0 | 0.001 | 0.31 | 0 | 0.011 | 0.001 | 0 | 0.1292 | 0 | 0.09 | 0.0346 | 0.22 | 0.0085 | 0.0002 | 0.017 | 0 | 0.0903 | 0.0278 | 0.101 | 0.028 | 0 | 0.122 | 0.06 | 0 | 0 | 0.0071 | 0.0091 | 0.005 | 0.0178 | 0.056
2019-07-21 22:00 | 167 | 0 | 0.0378 | 0.018 | 0.0008 | 0.059 | 0 | 0.2 | 0.0189 | 0.0029 | 0.09 | 0.024 | 0.004 | 0.067 | 0 | 0.001 | 0.2 | 0.001 | 0.009 | 0.001 | 0 | 0.0882 | 0 | 0.09 | 0.035 | 0.225 | 0.0087 | 0.0002 | 0.02 | 0 | 0.0932 | 0.0281 | 0.116 | 0.027 | 0 | 0.131 | 0.03 | 0 | 0 | 0.0091 | 0.0092 | 0.005 | 0.0176 | 0.056
2019-07-21 23:00 | 168 | 0 | 0.0358 | 0.0163 | 0.0007 | 0.06 | 0 | 0.1 | 0.0166 | 0.0028 | 0.05 | 0.038 | 0.005 | 0.067 | 0 | 0.001 | 0.1 | 0.001 | 0.009 | 0.019 | 0 | 0.0492 | 0 | 0.05 | 0.031 | 0.229 | 0.0076 | 0.0001 | 0.02 | 0 | 0.082 | 0.0249 | 0.115 | 0.03 | 0 | 0.134 | 0.04 | 0 | 0 | 0.0094 | 0.0106 | 0.005 | 0.016 | 0.055